THIRD ANGLE PROJECTION

THIS DRAWING TO BE REVISED IN MICROSOFT WORD ONLY.  THE SOURCE FILE IS STORED IN THE EDMS

CYBER SECURITY

| LIST OF COMPLEMENTARY DOCUMENTS |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | DWG. NO. |

TABLE OF CONTENTS

1.0	INTRODUCTION	5

1.1	Punch List Tabulation of Problem Reports	5

1.2	Error Correction / Retest	5

1.3	Change Management	5

1.4	Reference Documents	6

1.5	OTArmor Machine Roles 	6

2.0	REQUISITION INFORMATION	7

3.0	AGENDA	7

4.0	EQUIPMENT INSPECTION	7

4.1	Equipment Inspection	7

4.2	Remote Desktop to HMIs (Virtual machines only)	9

5.0	RADIUS	10

5.1	RADIUS Functionality	10

5.2	Verify RADIUS Account Login	12

5.3	Verify RADIUS Account Lockout	13

6.0	FIREWALL TESTING	14

Certificate Validation Use of HTTPS	14

6.2	Approved Use Banner (Optional)	15

6.3	Firewall Backup and Restore	16

6.4	Verify NIDS Configuration (Optional)	17

7.0	Cat Tools	18

7.1	Verify Network Switch is configured in CatTools	18

7.2	Verify Network Switch Backup Task in CatTools	19

7.3	Verify Configuration Changes are Identified	20

7.4	Verify the Network Switches can be restored using CatTools	21

7.5	Verify Network Switches have a customer approved banner during sign in (Optional)	22

7.6	Verify the Network Switches are synced to NTP source	23

7.7	Verify the Network Switches have a MAC address filter (Optional) (This is commercial offering only)	24

7.8	Disable any Unused Ports (Optional) based on the project scope this may be executed at the time of COD.	25

8.0	NTP	26

8.1	Verify NTP Synchronization	26

8.2	Verify Servers Sync to NTP Server (HMI’s Excluded)	27

9.0	Account Management	28

9.1	Default/Domain Accounts	28

9.2	Verify Operator Account	29

9.3	Verify Engineer/Maintenance Account	30

9.4	YubiKey (Optional)	31

9.5	Verify Shared Accounts	32

9.6	Service Accounts	33

9.7	Verify Service Account Restrictions	34

9.8	Verify Service Account Password Policy	35

9.9	Domain Password Policy Settings	36

9.10	Verify Password Policy on Domain Accounts	37

9.11	Verify Password Policy on Local Accounts	38

9.12	Account Lockout	39

9.13	Verify Account Reset after Lockout	40

10.0	Windows Patching	41

10.1	Patch Scan and Deployment	41

10.2	Verify Device Detection for Patching	42

10.3	Verify Patch Deployment	43

11.0	HMI Backup & Restore	44

11.1	Perform Backups	44

11.2	Verify Restore Activities for Files/Folders. (Optional)	45

11.3	Verify Restore Activities for Thick HMIs. (Optional)	46

11.4	Verify System After Restore.	47

12.0	WHAT’s UP GOLD (Optional)	48

12.1	Verify Credentials	48

12.2	Scan the network	49

12.3	Create New Scan	50

12.4	Verify Network Monitoring	51

13.0	NETWORK SECURITY MONITORING (Optional)	52

13.1	Monitoring Port	52

13.2	Nozomi Dashboard	53

13.3	Network Traffic Validation	54

13.4	Passive Monitoring and Network modeling and visualization Operation	55

13.5	Learning Mode Configuration	57

13.6	Malicious Signature detection	58

14.0	TRELLIX	59

14.1	Trellix Agent	59

14.2	Verify ePO Virus Definitions	60

14.3	Verify ePO Software Deployment	61

14.4	Verify Antivirus Software Operation	62

14.5	Verify Threat Event on LM1 (optional)	63

14.6	Verify Device Control Policy	64

14.7	Verify USB Device Access	65

14.8	Verify USB Device Restrictions	66

14.9	Verify USB Device Restrictions Event on LM1 (Optional)	67

14.10	SolidCore	68

14.11	Testing SolidCore Application	69

15.0	SIEM (Optional)	70

15.1	SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards	70

15.2	Verify Asset Listing	71

15.3	Verify Data Sources in Local Receiver – ELM.	72

15.4	Verify Event Logging	73

15.5	SIEM Report Generation	74

16.0	Trend Micro (Optional)	75

16.1	Verify Security Agent and Policy Status	75

16.2	Verify Pattern Update	77

16.3	Verify Update Endpoints	78

16.4	Verify AV Software Operation	79

16.5	Verify Device Control - USB Device Access	80

16.6	Application Control	82

17.0	Tripwire Industrial Visibility (Optional)	84

17.1	Verify Domain Integration	84

17.2	Verify Control Protocol Decoding	85

17.3	Verify Malicious Signature Detection	86

17.4	Verify Active Query Information	87

18.0	Controller Hardening 	89

18.1	Secure Mode	89

19.0	SPLUNK (Optional)	90

19.1	Verify Firewall Unsuccessful logins	90

19.2	Verify Devices are reporting to Splunk	91

19.3	Verify Successful/Unsuccessful login reporting	92

19.4	Verify NIDS is reporting	93

20.0	XONA (Optional)	94

20.1	Xona User Account Login	94

20.2	Xona Administrator Account Login	95

20.3	Xona File Transfer Test – SMB in SSL-VPN Tunnel	96

20.4	Xona File Transfer Test – Web Upload	98

20.5	Xona Web Portal Access Test - SSH Session / SMB Upload	100

20.6	Xona VNC Session Test	101

20.7	Xona Session Monitoring/Kill Test	102

20.8	FortiGate VPN Host Rejection Test	103

20.9	Xona Duration Testing	104

21.0	HIGH AVAILABILITY FAIL-OVER	105

22.0	AGREED RESIDUAL ACTIONS	106

23.0	CUSTOMER WITNESS TEST SIGNATURE SHEET	107

INTRODUCTION

This document describes the proposed Customer witness test (CWT) of the Cyber Security Management System.

The Customer witness test will take place in GE Vernova Facilities, during a period of 2 days. Testing will include hardware, software, and a documentation review of the system.  The intent of the test is to demonstrate that the system under test operates as designed. This document will be used as the approval document to provide a record of the test activities.

At the end of the CWT a summary of the test results and corrective actions will be added to this document and archived. Any items that cannot be resolved prior to shipment will be addressed by engineering and communicated to the site installation team prior to the unit outage by the most effective means possible.

Punch List Tabulation of Problem Reports

During the CWT test personnel will document any problems that require corrective action. The tester will identify their name, the date that the problem was found, any document references, and a description of the problem.

When problems are discovered, they will be reviewed with the engineer for that area. Problems and non-conformances shall be formally logged in Section  AGREED RESIDUAL ACTIONS.

The CWT owner or an engineer/technician under the direction of the CWT owner will implement all corrections. Problems will be considered resolved only when the engineer responsible for that area of the test signs them off. All problem reports must be resolved prior to authorization for shipment.

Error Correction / Retest

The timing of error corrections and retests will depend on the type and scope of the problems encountered. Problems that can be easily corrected will be corrected when identified and recorded in Section AGREED RESIDUAL ACTIONS. Problems that require more time to correct may be resolved and/or re-tested prior to shipment or as agreed between the parties.  Residual Actions may be moved to a Project Open Items List as a method of resolution as to not hold up completion of testing or shipment.

Replacement of any hardware, firmware or changes to the software configurations may require that the affected components or code be retested to ensure that the design remains valid as determined by the Test Engineer.  The retest will be performed using the relevant sections of this CWT procedure.

Change Management

A change management log will be used for the duration of the CWT. His log will track any changes made to the system that vary from the original configuration. All changes need to be approved by GEV and the customer. Logs will be recorded in the “Comments and Observations” of each task.

Reference Documents

The following is a list of reference documents used in conjunction with the Customer witness test the latest revisions of these documents will be used at the time of the test. The GE Cyber Engineer shall be responsible for obtaining the latest revisions.

- Network Topology (656B3021).

- GEV Controls Ports and Services Document (132M6452).

- Pre-CWT Ports and Services Scan Results.

Note: This document is a complete checklist for security features.  A project CWT checklist will be generated for the features included with a specific project."

OTArmor Machine Roles

1.5.1 DC1, DC2:

Primary and Secondary Domain Controllers. These machines manage authentication and configurations for other assets.

1.5.2 DR1:

Disaster Recovery. This machine hosts the CatTools and Acronis applications, which are used for backups and recovery.

1.5.3 PM1:

Patch Management. This machine hosts the Ivanti application, which is used for deploying Windows patches.

1.5.4 SP1:

System Protection. This machine hosts the Trellix Electronic Policy Orchestrator (ePO). The ePO is an agent-based software that manages Endpoint Security (Antivirus), SolidCore (Application Whitelisting) and DLP (Data Loss Prevention).

1.5.5 SIEM:

Security Information and Event Management. A Trellix non-Windows machine that is accessed via a web browser. OTArmor assets are configured to forward event logs to be centrally viewed and managed.

1.5.6 LM1:

A log management system is a system used to collect, store, process, and analyze log data from various IT systems and applications

1.5.7 NM1:

Centralized platform used to monitor, manage, and optimize a network's performance, security, and resource utilization

REQUISITION INFORMATION

Customer:   	Yanbu NGL

End User:   	Yanbu NGL

Site Name:	ARAMCO - Yanbu NGL

Project number #: F7391G13

GEV Control Personnel: <GE PERSONNEL>

AGENDA

EQUIPMENT INSPECTION

The following sections provide a brief description of the inspection / test. It also permits the recording of comments and allows sign off on each test.

Equipment Inspection

This task performs a visual inspection system or HMIs.

| Description | Comments & Observations |
| --- | --- |
| Perform a visual inspection of the system or HMIs. |  |
| Expected Result to pass: |  |
| All components are present and represented in the system drawings. |  |

Remote Desktop to HMIs (Virtual machines only)

This task defines if the HMIs will need to have Remote Access enabled. If the HMI’s to be installed at site are not present during the CWT, this task will be performed at site.

If the HMIs are present during the CWT and Remote desktop access is requested, in each HMI:

Navigate to “Control Panel -> System -> Remote Settings”.

Select “Allow remote connections to this computer”.

If possible, select “Allow connections only from computers running Remote Desktop with Network Level Authentication (recommended)”. There may be cases when connecting to an older computer may need to leave this unchecked.

The following services must be turned on for remote desktops to work:

Navigate to “Control Panel -> Administrative Tools -> Services”.

Find the “Remote Desktop Services Service”, enable it and place it in automatic.

Find the “Remote Desktop Services User Mode Port Redirector”, enable it and place it in automatic. Start this service.

Verify Remote Desktop is added in the Windows Firewall:

Navigate to “Control Panel -> Windows Firewall -> Allow an app or feature through Windows Firewall”.

On the list displayed look for “Remote Desktop” and make sure “Domain” and “Private” are checked. If not, proceed to click on “Change Settings” and check “Domain” and “Private” and click “OK”.

Verify that RDP connections are successful.

NOTE. If RDP is not required by the customer or not needed anymore, disable Remote Desktop in the Windows Firewall.

| Description | Comments & Observations |
| --- | --- |
| If required, verify Remote Desktop is enabled on all HMIs. |  |
| Expected Result to pass: |  |
| Verify we can Remote Desktop into the HMI’s configured. |  |

RADIUS

RADIUS Functionality

This task is to verify the network switches that have been entered in Radius, this test will be performed Domain all Controllers:

Log into one of the DC using an administrator account and Launch the Server manager, open “Tools->Network Policy Server”.

Expand “RADIUS Clients and Servers” and select “RADIUS Clients” and verify the Network Switch are present as per Network Topology.

Disable the Network Policy Server on Domains.

Attempt to authenticate to the Network Switch, verify that the radius services can NOT successfully authenticate the “GESwitch & GEswitchOper” account.

Attempt to log onto the Network Switch using the local account ‘Admin’ and verify it is successful.

Enable the Network Policy Server on Domains.

Attempt to authenticate to the Network Switch, verify that the radius services can successfully authenticate the “GESwitch & GEswitchOper” account.

Attempt to log onto the Network Switch using the local account ‘Admin’ and verify it is unsuccessful

| Description | Comments & Observations |
| --- | --- |
| Review RADIUS in Active Directory on all Domain Servers to verify Network Switch is entered. When “Network Policy Server” is Disable verify: - Unsuccessful access occurs with “GESwitch & GEswitchOper” when trying to login into Network Switch. - Successful access occurs with Local “Admin” Account when trying to login into Network Switch. When “Network Policy Server” is started, verify: - Unsuccessful access occurs with Local “Admin” when trying to login into Network Switch. - Successful access occurs with “GESwitch & GEswitchOper” Account when trying to login into Network Switch. |  |
| Expected Result to pass: |  |
| - Confirm Domain Servers have the Network Switch(es) configured in Radius. - Confirm you can authenticate with the GESwitch & GEswitchOper user account in the Network Switch when the Network Policy Server is running. Confirm authentication fails when the Network Policy Server is NOT running. - Confirm you can authenticate with the Local Admin user account in the Network Switch when the Network Policy Server is NOT running. Confirm authentication fails when the Network Policy Server is running. |  |

Verify RADIUS Account Login

This task is to verify the Network Switch can be accessed with a Network Domain Account ‘GESwitch & GEswitchOper’:

Log into the DR1 using an administrator account and launch the PuTTY shortcut on the desktop.

Enter the information to connect to a Network Switch and login with the “GESwitch & GEswitchOper” credentials.

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switch can be accessed with the Active Directory account ‘GESwitch & GEswitchOper’. |  |
| Expected Result to pass: |  |
| Successful login with GESwitch & GEswitchOper account. |  |

Verify RADIUS Account Lockout

This task is to verify a domain account will be locked after 10 failed attempts using RADIUS:

Log into the DR1 using an administrator account and launch the putty shortcut on the desktop, Provide IP address/Hostname details and click on ok to open session.

Enter the correct Username but an incorrect password for the GESwitch & GEswitchOper account. Make sure you try these 10 times. (If Putty shows an error, please close Putty and open again).

After 10 tries, type the correct password. It should still report you are not able to log into the system.

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name(HMI.local)->GEV Controls->GEV Users and Computers”. Look for GESwitch & GEswitchOper Account and double click it.

Click on the “Account” tab, you will see the account is being locked. Check “Unlock Account” and click OK.

Try to login into Network Switch using Putty with the correct Credentials and password. Confirm the account can login successfully.

| Description | Comments & Observations |
| --- | --- |
| Verify the GESwitch & GEswitchOper account is locked when entering 10 bad passwords. Reset the account, log in successfully. |  |
| Expected Result to pass: |  |
| Verify Account locks after 10 fail attempts. Also verify you can login successfully after resetting the account. |  |

- FIREWALL TESTING

- Certificate Validation Use of HTTPS

This task is to verify the firewall can be connected using HTTPS Vs HTTP:

    - Open Chrome from DR1 Server. In the browser type: “https://<name of firewall or IP Address> <enter>. Confirm you are prompted to log into the firewall.

    - Open another tab in Chrome and in the browser type: “https://<name of firewall or IP Address> <enter>. Confirm the page does not load.

    - Open CLI and execute the command below to verify certificate validity.

- diagnose sol certificate list

| Description | Comments & Observations |
| --- | --- |
| Verify the firewall is accessed using HTTPS and verify ssl certificate |  |
| Expected Result to pass: |  |
| Verify access is possible using HTTPS and found valid certificate. |  |

  - Approved Use Banner (Optional)

This task is to verify the right banner that has been applied into the firewall. Banner should have been provided by the client. If a banner is not provided, this test will verify that a banner can be displayed:

    - Open Chrome from DR1. In the browser type: “https://<name of firewall or IP Address>” <enter>.

    - A banner should be shown before you are able to login into the system.

| Description | Comments & Observations |
| --- | --- |
| Verify proper banner is displayed when attempting to log into the firewall. |  |
| Expected Result to pass: |  |
| Verify the banner is presented before being permitted to login into the firewall. (Only if banner was given by client). |  |

  - Firewall Backup and Restore

This task is to verify the firewall can be backed up and restored from a previous backup.

Backup:

    - Log into the DR1 using an administrator account and launch the kiwi CatTools application.

    - Execute a backup task for the Fortinet in the “Activities” tab.

    - Verify that the task completes successfully, and a current backup file is obtained.

    - Verify a scheduled task exists to perform a backup of the Fortinet device in the validation lab.

Restore:

    - Log into the DR1 using an administrator account and launch the Firewall shortcut on the desktop / open browser and type: “https://<name of firewall or IP Address>” <enter>. .

    - Modify the host name of the firewall to be something other than the current name.

    - Click the user (Top right) -> Configuration -> Restore.

    - Make sure we restore from “Local PC”, under File click on “+Upload”. Browse where we have the backup we want to restore with.  Leave password in blank and click ok.

    - Verify the restore has been done successfully by confirming the firewall has the proper hostname.

| Description | Comments & Observations |
| --- | --- |
| Verify firewall can be backed up using CatTools and restored from the firewall GUI. |  |
| Expected Result to pass: |  |
| Verify the backup file has been generated successfully and it can be accessed. Verify the restore has been deployed successfully. |  |

  - Verify NIDS Configuration (Optional)

    - Generate several NIDS strings in the system (Test-NIDS2.ps1) Open file explorer and type this path:\\CA1\Admin_Procedures\OTArmor on any of the HMIs and take note of the time they were executed. This PowerShell will simulate an attack in the system.

    - Log into the firewall and under Network->Interfaces check the port is configured for NIDS.

    - Also, under Log&Report->Intrusion Prevention, verify you got the logs for the attack (Test-NIDS2.ps1).

    - “GEV NIDS TEST STRING” is the string that will be listed in the logs. Verify time matches with the ones you executed and from the devices they were executed.

- Note. This step will be verified a 2nd time if you have LM1.

| Description | Comments & Observations |
| --- | --- |
| Verify “GE NIDS TEST STRING” can be found in the local logs after executing Test-NIDS2.ps1. |  |
| Expected Result to pass: |  |
| Verify the Firewall is receiving “GE NIDS TEST STRING” logs and they match the ones that were executed with Test-NIDS2.ps1. |  |

- Cat Tools

Verify Network Switch is configured in CatTools

This task is to verify Network Switch configured in CatTools:

Log into the DR1 using an administrator account and launch the CatTools shortcut on the desktop.

On the left panel you, under the “Devices” tab, a list of devices will be listed. Please verify the Network Switch is listed with its correct IP Address.

| Description | Comments & Observations |
| --- | --- |
| Verify the network switch is listed in CatTools. |  |
| Expected Result to pass: |  |
| In the list of devices, the network switch(es) will be present with correct IP Address(es). |  |

Verify Network Switch Backup Task in CatTools

This task is to verify network switch can be backed up using CatTools:

Log into the DR1 using an administrator account and launch the CatTools shortcut on the desktop.

On the right Panel, under “Activities” Tab, look for the “Backup Activity”.

Right click on the task and choose “Run Now”.

On the bottom panel, you will see and “Activity Log”, it will inform you how the activity is running and if it founds any error while executing. (Please be patient, getting a backup can take up to 5 to 10 minutes). Once the task is finished, the logs will report if the task is finished successfully or with errors.

When task finishes running successfully, go to the “File Explorer” and browse to the following path: “C:\Backups\Switches\Config”. It should list a file with the name “Config.Current.Running. [Name of Network Switch].txt”.

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switch(es) can be backed up in CatTools. |  |
| Expected Result to pass: |  |
| Backup tasks will run successfully, and a file will be created under C:\Backups\Switches. |  |

Verify Configuration Changes are Identified

This task is to verify Network Switch changes can be tracked using CatTools:

Log into DR1 using an administrator account.

Execute a backup task on the Network Switch.

After the backup task is complete, log into the Network Switch and perform a configuration change.

Re-execute the backup task in CatTools.

Open File Explorer and navigate to “C:\Backups\Switches\Reports\ConfigChanges”.

A list of files will be shown, open the latest one by double clicking it.

Review the Report and verify that the report identifies what was changed on the Network Switch.

| Description | Comments & Observations |
| --- | --- |
| Use the reports function to verify any network switch changes that can be documented. |  |
| Expected Result to pass: |  |
| The CatTools application will identify the changes made to the device under test. |  |

Verify the Network Switches can be restored using CatTools

This task is to verify the Network Switches can be restored using CatTools:

Log into the DR1 using an administrator and launch the CatTools shortcut on the desktop.

Verify the selected Config file from the “C:\Backup\Switches\Config” folder is put into the “C:\Backup\Switches\Restore” folder

On the right panel in CatTools, under the “Activities” tab, a list of Activities will be listed. Double click on the “Restore Network Switch”.

Verify the Network Switch gets restored to the selected configuration.

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switches can be restored to a previous configuration using CatTools. |  |
| Expected Result to pass: |  |
| Verify the Network Switch has been restored to its selected configuration successfully. |  |

Verify Network Switches have a customer approved banner during sign in (Optional)

This task is to verify the Network Switches have a customer approved banner during sign in:

Log into the DR1 using an administrator.

Open File Explorer and navigate to “C:\Backup\Switches\Config”. Open the config of the Network Switches and review the file for the customer approved banner.

Verify the Network Switch has the customer approved banner.

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switch displays the customer approved banner during sign in. |  |
| Expected Result to pass: |  |
| Verify the Network Switch displays the customer approved banner. |  |

Verify the Network Switches are synced to NTP source

This task is to verify the Network Switches sync to the proper NTP source:

Log into the DR1 using an administrator account and launch the CatTools shortcut on the desktop.

On the left panel, under the “Devices” tab, a list of devices will be listed. Double click on the Network Switch device listed.

Login to the Network Switch and verify the switch has the correct NTP Source at the end of the config.

Verify NTP status of the switch “show ntp status”

Verify NTP associations of the switch “show ntp associations”

Verify Switch time “show Clock”

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switches are synced to the correct NTP Source at the end of the config.sh | NTP Source: _____________________________ |
| Expected Result to pass: |  |
| Verify the Network Switches have the correct NTP source added successfully at the end of the config. |  |

Verify the Network Switches have a MAC address filter (Optional) (This is commercial offering only)

If requested, this task is to verify the Network Switches have a MAC address filtering and the filter is being applied to the correct switch ports:

Log into the DR1 using an administrator.

Open File Explorer and navigate to “C:\Backup\Switches\Config”. Open the config of the Network Switches and review the file looking for the MAC Filtering list and the list applied to the switch ports.

Login into the Network Switch and verify the switches have MAC Address filtering applied to its ports.

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switches have MAC Address filtering list applied and that the list is being applied to the appropriate ports. |  |
| Expected Result to pass: |  |
| Verify the Network Switches have MAC Address filtering list applied and that the list is successfully being applied to the ports. |  |

Disable any Unused Ports (Optional) based on the project scope this may be executed at the time of COD.

If requested, this task is to verify the Network Switches have the appropriate unused ports disabled.

Log into the DR1 using an administrator.

Open File Explorer and navigate to “C:\Backup\Switches\Config”. Open the config of the Network Switches and review the file looking for the unused ports with the shutdown command applied.

Sign into the Network Switch and verify the applicable ports have had the shutdown command applied to the unused ports.

| Description | Comments & Observations |
| --- | --- |
| Verify Network Switches have any unused ports shutdown. |  |
| Expected Result to pass: |  |
| Verify the Network Switches have successfully shutdown the appropriate unused ports. |  |

NTP

Verify NTP Synchronization

This task is to verify if the domains are synced to the proper NTP Server:

Log into the DC using an administrator account.

Open the Admin Command Prompt and type: “w32tm /query /peers” <Enter>

Verify the system is pointing to the correct NTP IP Address.

| Description | Comments & Observations |
| --- | --- |
| Verify DC1/ DC2 is synced to the proper time source. | NTP Source: ______________ |
| Expected Result to pass: |  |
| Verify the Domain Server is pointing at the correct time source. |  |

Verify Servers Sync to NTP Server (HMI’s Excluded)

This task is to verify if the Servers are synced to the Active Domain Controller:

Log into each Servers using an administrator account.

Open the Admin Command Prompt and type: “w32tm /query /peers” <Enter>.

Verify the system is pointing to the Active Domain Controller IP Address.

| Description | Comments & Observations |
| --- | --- |
| Verify all Servers are synced to DC1. |  |
| Expected Result to pass: |  |
| Verify the servers are pointing at the correct Active Domain Controllers. |  |

Account Management

Default/Domain Accounts

This task is to verify only the applicable Users are enabled in the Domain and in HMI/Servers/NTP/Default Switches:

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers”Select “Tools->Active Directory Users and Computers” and review the Windows user accounts present.

Verify only necessary accounts are present and enabled. Default windows accounts not required are disabled or removed.

To check the local Users on the HMIs/Servers:

Log into the HMI and open “Control Panel -> All Control Panel Items-> Administrative Tools -> Computer Management -> Local Users and Groups -> Users”.

Review the windows user accounts present.

Verify only necessary accounts are present and enabled. Default windows accounts not required are disabled or removed.

| Description | Comments & Observations |
| --- | --- |
| Verify Windows default accounts have been deleted, disabled or renamed on the HMIs, Default Switches, NTP Server and Servers. |  |
| Expected Result to pass: |  |
| All the Accounts that are not going to be used should be disabled. In the comments list all the accounts disabled. |  |

Verify Operator Account

This task is to verify the Operator account settings to comply with Customer needs:

Log into the HMI using the GEOper account.

Verify the privileges that the account has:

Verify there is no access to the Command Prompt, no ability to Navigate to the hard drives, and cannot Open the Control Panel.

If needed, make changes on the account and describe them under “Comments & Observations”.

| Description | Comments & Observations |
| --- | --- |
| Verify ‘Operator’ account has least amount of user privileges. Accounts should not have any Admin rights. |  |
| Expected Result to pass: |  |
| Verify Operator Account does not have an Administrator Account. |  |

Verify Engineer/Maintenance Account

This task is to verify the Engineer/Maintenance account settings comply with Customer needs:

Log into the HMI using the GEMaint account.

Verify the privileges of the account by:

Opening the Command Prompt, navigate to the C: drive, Verify the. TCW is not in “Read-Only” mode, Open Control Panel and verify user has access and can make changes.

If needed, make changes on the account and describe them under “Comments & Observations”.

| Description | Comments & Observations |
| --- | --- |
| Verify ‘Engineer/Maintenance’ account has the right user privileges. Account should have Maintenance rights. |  |
| Expected Result to pass: |  |
| Verify Engineer/Maintenance Account has Command Prompt, Control Panel Access, can make changes in the E: Drive and. TCW. |  |

YubiKey (Optional)

Verify a secure connection can be made using YubiKey Two Factor Authentication.

    - At the Logon into an HMI (Only for physical HMIs):

      - Insert the YubiKey into the USB port on the HMI.

      - When Prompted for the YubiKey PIN and password, proceed to insert the credentials.

      - Verify a secure connection can be made for the user.

    - Launch the YubiKey Manager to verify the user has been issued a YubiKey Certificate:

      - Click “Start -> Yubico -> YubiKey Manager”.

      - When the application opens select “Applications -> PIV”.

      - Verify a YubiKey Certificate is issued for the logged in user.

| Description | Comments & Observations |
| --- | --- |
| Verify a secure session can relate to the YubiKey. |  |
| Expected Result to pass: |  |
| Verify a secure YubiKey session has been made and that a certificate is being issued for the logged in user. |  |

Verify Shared Accounts

This task is to verify all shared accounts:

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Select “Tools->Active Directory Users and Computers” and identify which users are shared Accounts. (A shared Account is when more than one person can access and login with an account).

- Standard default shared accounts are mentioned below

- GEAdmin

- GEMaint

- GEOper

| Description | Comments & Observations |
| --- | --- |
| Identify any shared accounts and if they are needed. |  |
| Expected Result to pass: |  |
| List under comments all the shared Accounts found. |  |

Service Accounts

This task is to verify all service accounts:

Log into any of the DC using admin account and launch “Server Manager”.

Select “Tools -> Group Policy Management”.

Under “Domain Name (HMI.local)-> GEV Controls->Domain Controllers ->GEV DCx Hardening Policy”. Select “Settings” tab and review the service accounts listed under “Deny Log on Locally”. Verify the User Group “Deny Log Locally” is listed.

Under “Domain Name (HMI.local)-> GEV Controls -> HMI->Windows 10 HMI -> GEV Win10 Hardening Policy”. Select “Settings” tab and review the service accounts listed under “Deny Log on Locally”. Verify the User Group “Deny Log Locally” is listed.

Under “Domain Name (HMI.local)-> GEV Controls -> OTArmor Servers-> GEV Server OS Hardening Policy”. Select “Settings” tab and review the service accounts listed under “Deny Log on Locally”. Verify the User Group “Deny Log Locally” is listed.

Select “Tools -> Active Directory Users and Computers”. Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Select “Tools->Active Directory Users and Computers”. Double click “Deny Log Locally” User group and choose “Member of” tab. Verify the list of users.

| Description | Comments & Observations |
| --- | --- |
| Identify any accounts associated with automated functions. |  |
| Expected Result to pass: |  |
| List under comments all the service Accounts found. |  |

Verify Service Account Restrictions

This task is to verify all service accounts cannot login into windows locally:

Log into the HMI trying to use any of the service accounts.

A message stating the Account cannot be log in should appear.

| Description | Comments & Observations |
| --- | --- |
| Verify these accounts cannot be used to log into Windows: • “Deny Log on Locally” is set |  |
| Expected Result to pass: |  |
| Login should fail with a message stating the account is a service Account. Record the name of the account(s) tested. |  |

Verify Service Account Password Policy

This task is to verify all service accounts have their password set to never expire:

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Select “Tools->Active Directory Users and Computers” and identify a service Account.

Double click it and under” Account” tab (in the Account Options), make sure “Password Never Expires” is checked.

| Description | Comments & Observations |
| --- | --- |
| Verify these accounts have their passwords set to never expire. |  |
| Expected Result to pass: |  |
| Each Account should show the ‘Password never expires’ checked. Record the name of the account(s) tested. |  |

Domain Password Policy Settings

This task is to verify the Domain Password Policies are setup correctly:

    - Log into any of the Domain controllers using admin accounts.

    - Open “Server Manager”.

    - Select “Tools -> Group Policy Management”.

    - Expand “Forest. Domain Name (HMI.local) -> Domains -> Domain Name (HMI.local)-> GEV Site Customization Policy

- ” And click “Edit”. Expand the following path “Computer configuration-> Policies-> Windows Settings->Security Settings -> Account Policies -> Password Policy”.

Verify each of the items listed below and make sure the settings are correct on the policies mentioned above:

- Enforce Password History = 24 Passwords

- Maximum Password Age = 90 Days

- Minimum Password Age = 1 Day

- Minimum Password Length = 8 Characters

- Password must meet complexity requirements = Enabled

| Description | Comments & Observations |
| --- | --- |
| Verify OTArmor Domain Policy password policy is set to: Enforce Password History = 24 Passwords Maximum Password Age = 90 Days Minimum Password Age = 1 Day Minimum Password Length = 8 Characters Password must meet complexity requirements = Enabled |  |
| Expected Result to pass: |  |
| Make sure each setting is correctly set as per list above. |  |

Verify Password Policy on Domain Accounts

This task is to verify the Password Policy is enforcing the passwords in new domain accounts:

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Right click on “GEV Users and Computers”, then choose “New -> User”.

Select a name for the username and click “Next”. Enter a simple password to test the enforcement and click “Next” and then “Finish”. An error pops up will appear stating the password does not meet the Password Policy requirement.

Attempt to set the user password again, this time apply a complex password meeting the settings on previous step.

Verify the user password is accepted.

Delete the account after the password is verified.

| Description | Comments & Observations |
| --- | --- |
| Create a dummy domain account and test password policy is being enforced. Delete account when finished. |  |
| Expected Result to pass: |  |
| Verify the account can be created when the password meets the password enforcement established on the Domain. |  |

Verify Password Policy on Local Accounts

This task is to verify Password Policy enforcing the password in new local accounts:

Log into an HMI using admin account.

Open “Control Panel -> All Control Panel Items-> Administrative Tools -> Computer Management -> Local Users and Groups -> Users”. Right click on “Users”, then choose “New User”.

Select a name for the username and click “Next”. Enter a simple password to test the enforcement and click “Next” and then “Finish”. An error pops up will appear stating the password does not meet the Password Policy requirement.

Attempt to set the user password again, this time apply a complex password meeting the Password Policy settings above.

Verify the user password is accepted.

Delete the account after the password is verified.

| Description | Comments & Observations |
| --- | --- |
| Create a dummy HMI local account and test password policy is being enforced. Delete account when finished. |  |
| Expected Result to pass: |  |
| Verify the account can be created when the password meets the password enforcement criteria established. |  |

Account Lockout

This task is to verify any user can be locked out after 10 failure login attempts:

Choose an account other than the Administrator account and attempt to login to a server with a wrong password. Repeat this step 10 times.

After the 10th failure, attempt to login with the correct password. A message should appear stating the Account has been locked due to many unsuccessful attempts.

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Look for the User used on first step.

Once you find the User, right click on it and choose “Properties”. Under the account tab, a message will appear stating the account is locked.

Log out of the Domain Controller.

| Description | Comments & Observations |
| --- | --- |
| Verify if the incorrect password is entered more than 10 times a user account is locked out. | Account Tested: ____________ |
| Expected Result to pass: |  |
| Verify the account is locked out after 10 unsuccessful attempts. |  |

Verify Account Reset after Lockout

This task is to verify any user locked out can be reset and log in again:

Identify the account locked out in Test cases section 9.12

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers”. Look for the User you use on first step.

Once you find the User, right click on it and choose “Properties”. Under the account tab, a message will appear stating the account is locked

Check the “Unlock Account” and click OK.

Try to login with this user with the correct password. This time you should be able to login.

| Description | Comments & Observations |
| --- | --- |
| Verify account can be reset after lockout. | Account Tested: ___________ |
| Expected Result to pass: |  |
| Verify the account is reset and can login again. |  |

Windows Patching

Patch Scan and Deployment

This task is to verify the latest PVP disk has been deployed in PM1:

If you have application control, make sure to change Policy to Patching or Update mode in Trellix EPO. If not, directly proceed with the following steps.

Obtain the updated PVP patch disk or associated .iso file.

Mount the patch disk and execute the update batch file.

Verify the process completes successfully.

| Description | Comments & Observations |
| --- | --- |
| Verify latest GE approved patches are deployed to the Ivanti Console. Update discs will always be one month behind. | Version Used: ____________ |
| Expected Result to pass: |  |
| Verify the PVP disk run successfully. |  |

Verify Device Detection for Patching

This task is to verify all the devices that are detected by Ivanti in PM1 Server:

Log into the PM1 server using an administrator account and launch the Ivanti shortcut on the desktop.

Perform a patch scan of the Domain using the pre-defined GE patch list.

Verify Ivanti lists all the HMIs, Servers (Virtual Machines) in the system.

Machine Groups as follows

- 11.3.4.1 OTArmor Servers Group:

- CA1

- DC1

- DR1

- PM1

- SP1

- 11.3.4.2 OTArmor Early Adopters:

- DC2

- 11.3.4.3 HMIs:

- All other physical and virtual machines

| Description | Comments & Observations |
| --- | --- |
| Verify all HMIs, servers: virtual machines are reporting in the Ivanti console. |  |
| Expected Result to pass: |  |
| After the scan, verify all the devices are listed. |  |

Verify Patch Deployment

This task is to verify all the devices that are detected by Ivanti in PM1 Server, and we can deploy patches into them:

Log into the PM1 server using an administrator account and launch the Ivanti shortcut on the desktop.

Perform a patch scan of the Domain using the pre-defined GE patch list.

Verify it lists all the HMIs, Servers (Virtual Machines) in the system.

Deploy all missing patches in a chosen HMI/Server. Verify that a “Patching in progress” message is displayed on the target machines.

If necessary, reboot the systems being patched when the patches complete deploying.

Perform a patch scan of the HMI/Server chosen using the pre-defined GE patch list, verify that the patches deployed no longer show as required.

If any new patches show as required, deploy the patches to the systems. If necessary, reboot the systems being patched when the patches complete deploying.

Repeat this process and verify the systems can be patched with no missing patches present.

| Description | Comments & Observations |
| --- | --- |
| Scan the network and deploy any missing patches or service packs. Reboot HMIs/Servers as necessary. |  |
| Expected Result to pass: |  |
| Verify patches can be deployed in devices listed on Ivanti console. |  |

HMI Backup & Restore

Perform Backups

This task is to verify Acronis has the backup plans set for all HMIs\Servers:

Log into the DR1 system using an administrator account and connect to Acronis Management Server.

Select Backup Plans.

Make sure we have defined a Backup Plan for OTArmor Servers.

Make sure we have defined a Backup Plan for HMIs

On each backup plan verify the configuration of it. Right click on the backup plan and choose “Edit”.

The backup plan configuration determines the rate of backups, as well as how long they are kept. There are three types of backups:

- 12.1.5.1 Full – A complete backup of the machine.

- 12.1.5.2 Differential – A backup of changes that have occurred since the last Full backup.

- 12.1.5.3 Incremental – A backup of changes that have occurred since the last Differential backup.

There is a plan present for every asset.

All plans present a green status.

What to back up: Entire Machine

Where to back up: //NAS/Backup

How long to keep:

Full: 6 Months

Differential: 4 Weeks

Incremental: 7 Days

| Description | Comments & Observations |
| --- | --- |
| Verify all HMIs/Servers are in the backup plan in the Acronis Management Console. |  |
| Expected Result to pass: |  |
| Verify back up plans were created that includes all the Windows devices. |  |

Verify Restore Activities for Files/Folders. (Optional)

This task is to verify Acronis can restore Files /Folders.

Log into the DR1 system using an administrator account and connect to the Acronis Management Server.

Select DR1 on the All-Devices page.

Choose the Recovery > Recover… > Files/Folders option on the right:

Select C:\bginfo\ and select Download from the right.

Once the download is completed, verify that the folder can be opened, and the image inside can be viewed.

| Description | Comments & Observations |
| --- | --- |
| Verify an HMI files/Folders can be restored in case of a disaster recovery by using the Acronis backup | HMI Restored: ____________ |
| Expected Result to pass: |  |
| Verify Acronis Restore executes successfully. Take note of the Files/Folders restored under Comments & Observations. |  |

Verify Restore Activities for Thick HMIs. (Optional)

This task is to verify Acronis can restore an HMI:

Log into the DR1 system using an administrator account and connect to the Acronis Management Server.

Create recovery media in the Acronis console in the CD format.

Select an HMI to recover, record the machine name below.

Log into the machine to be recovered. Execute an incremental backup of the machine.

When the backup is complete, create a file on the computer desktop.

Reboot the system to the physical CD recovery media, restore the most current backup of the virtual system.

When the recovery is complete, log into the system and verify the file doesn’t exist on the desktop.

| Description | Comments & Observations |
| --- | --- |
| Verify an HMI can be restored in case of a disaster recovery by using the Acronis Boot Disc. | HMI Restored: ____________ |
| Expected Result to pass: |  |
| Verify Acronis Restore executes successfully. Take note of the HMI restored under Comments & Observations. |  |

Verify System After Restore.

This task is to verify functionality after the restore:

Log into the HMI/Server restored using an administrator account.

Verify the name of the HMI and IP Address.

Log into PM1 using an administrator account, verify Ivanti can scan the HMI/Server..

Log into LM1 using an administrator account, verify Splunk can receive logs from the HMI/Server.

Log into DR1 using an administrator account, verify Acronis can scan the HMI/Server.

| Description | Comments & Observations |
| --- | --- |
| Verify the following after the restore is complete: • Machine name and IP address are correct • HMI is reporting in McAfee/Trend Micro/Splunk, Acronis and Ivanti. |  |
| Expected Result to pass: |  |
| Verify name and IP Address are correct in the HMI restored. Verify HMI is recognized by our different Server applications. |  |

WHAT’s UP GOLD (Optional)

Verify Credentials

This task is to verify all the credentials that have been created to access the network:

Log into the NM1 server using an administrator account and launch the web management interface shortcut on the desktop.

Log in using the admin account.

Access the “Settings->Libraries->Credentials” and verify SNMPv3, SSH, VMWare & Windows credentials are created.

| Description | Comments & Observations |
| --- | --- |
| Verify all Credentials are created for the different types of assets in the system. |  |
| Expected Result to pass: |  |
| Verify SNMPv3, SSH, VMWare & Windows credentials are created. |  |

Scan the network

This task is to scan the network to see all the devices in the system:

Log into the NM1 server using an administrator account and launch the web management interface shortcut on the desktop.

Log in using the admin account.

Access the “Discover->Saved Scan Settings”. In the list choose the “Full Network Scan” and click “Scan now”.

Wait until the scan is done. Then verify all the devices listed are the ones you have in your network topology.

Also verify the credentials are successful for the devices.

Check the devices that need to be monitored and add them to monitoring.

| Description | Comments & Observations |
| --- | --- |
| Scan the network and verify all the devices on the PDH network are visible according to the network topology. |  |
| Expected Result to pass: |  |
| All devices connected to PDH were scanned and monitored. |  |

Create New Scan

This task is to create a scan for the network to see all the devices in the system:

Log into the NM1 server using an administrator account and launch the web management interface shortcut on the desktop.

Log in using the admin account.

Access the “Discover->New Scan”. In the list choose the settings you want to scan and run it.

Wait until the scan is done. Then verify all the devices listed are the ones you have in your network topology.

| Description | Comments & Observations |
| --- | --- |
| Create Scan and verify all the devices on the PDH network are visible according to the network topology. |  |
| Expected Result to pass: |  |
| Verify Scan has been created, and it scanned the devices connected to PDH were scanned. |  |

Verify Network Monitoring

This task is to verify the different devices scanned and the topology:

Log into the NM1 server using an administrator account and launch the web management interface shortcut on the desktop.

Log in using the admin account.

Go to “My network”. Click on the “Auto Layout” and verify the network topology created.

Click in some of the devices and on the right menu click on the “Status” icon in the shape of a heart and verify the different variables brought by device.

Also right click in some of the devices and choose “Device Properties”. Verify the settings the properties bring per type of device.

| Description | Comments & Observations |
| --- | --- |
| Verify all devices are being monitored and check the status and properties for every type. |  |
| Expected Result to pass: |  |
| Verify all devices connected to the PDH are present and bringing status and properties. |  |

NETWORK SECURITY MONITORING (Optional)

Monitoring Port

Physically verify Nozomi device connections.

Verify if the ports are connected to a span port in the switches.

Connect to the switches through DR1/CatTools and verify if that port is a SPAN Port.

| Description | Comments & Observations |
| --- | --- |
| Ensure that Nozomi Guardian ports are connected to the span port of network switch. |  |
| Expected Result to pass: |  |
| Verify SPAN port is configured in switch through CatTools and is there’s a connection to the Nozomi Guardian as per Topology. |  |

Nozomi Dashboard

Open a web browser and connect to Nozomi.

Verify if dashboard is populating data.

| Description | Comments & Observations |
| --- | --- |
| Verify if data is populated in the Dashboard (Assets, Nodes, Sessions). |  |
| Expected Result to pass: |  |
| Data is shown in Nozomi Dashboard. |  |

Network Traffic Validation

This task is to Verify the appliance is observing Network Traffic

On the web GUI, go to Administration > Network Interfaces. Make sure that the Throughput graph is being updated live with network data from all the applicable monitoring interfaces.

On the web GUI, go to Environment > Network view > Traffic tab. Make sure that the graphs are getting populated with live data information.

| Description | Comments & Observations |
| --- | --- |
| Verify if the network traffic in network view Traffic tab populated live data information |  |
| Expected Result to pass: |  |
| Can see live data information in traffic tab. |  |

Passive Monitoring and Network modeling and visualization Operation

This task is to verify that Nozomi IDS appliances show assets in the network with correct information.

On the Network View > Nodes tab, verify that this data is getting populated:

- Address

- Role

- Type

- MAC address

- Protocols

- On the Asset view, verify that this data is getting populated:

- Name

- Address

- Role

- Type

- OS/Firmware

On the Network View > Links tab, verify this data is getting populated:

- From

- To

- Protocol

- First Activity

- Last Activity

- Throughput

On the Network View > Session’s tab, verify that this data is getting populated:

- Status (review that you have sessions with Status SYN, ACTIVE and CLOSED)

- From

- To

- Protocol

On the Network View > Graph tab, check that the network graph is being displayed. Apply various filters

| Description | Comments & Observations |
| --- | --- |
| Verify that Nozomi IDS appliance shows assets in the network with correct information |  |
| Expected Result to pass: |  |
| Can see live data populated in network view |  |

Learning Mode Configuration

This task is to verify Nozomi IDS appliance is configured in Learning mode.

Login to Nozomi web interface

Select Administration-> Security Control Panel->

Click on “1-Learning” on left-hand pane

Under “Phase Switching”, select “Two Phase” and then “Learning”

Click “Save”

| Description | Comments & Observations |
| --- | --- |
| Verify that Nozomi IDS appliance is configured in Learning mode |  |
| Expected Result to pass: |  |
| Can see Nozomi IDS appliance is configured learning mode |  |

Malicious Signature detection

Open a web browser and connect to Nozomi.

Copy Antivirus file and proceed to copy through the network to another asset.

Very Nozomi triggers an alert.

| Description | Comments & Observations |
| --- | --- |
| Verify the popup warning is presented after copying the Test Virus file to a remote system. |  |
| Expected Result to pass: |  |
| Alert triggered after copy of virus file via network. |  |

TRELLIX

Trellix Agent

This task is to verify all the devices that are detected by Trellix ePO in SP1:

Log into the SP1 using an administrator account and launch the Trellix ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Confirm that the machines with the System Tree are organized into the correct groups and appear as ePO managed endpoints

HMIs

OTArmor Servers

| Description | Comments & Observations |
| --- | --- |
| Verify all HMIs and Virtual machines are reporting in the Trellix Management Console. |  |
| Expected Result to pass: |  |
| Verify all the devices are listed in the Trellix ePO management console. |  |

Verify ePO Virus Definitions

This task is to update the virus definitions and verify the version of AV in Trellix ePO in SP1

Log into the SP1 using an administrator account and launch the Trellix ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “Menu -> Software-> Master Repository”. Click “Check In Package”.

Select Product or Update (.zip) as the package type and browse to select the package with the new definitions and select “Open”

Click Next to view the package check-in summary information.

Select “Branch -> Current”.

Click “Save” to begin the check-in. Wait until the Check-in is complete and click Close.

Ensure the new virus definition package is in the repository:

Click “Menu->Software->Master Repository”.

Search the DAT in the name column.

Verify that the DAT version displayed is the same as the version you checked in.

| Description | Comments & Observations |
| --- | --- |
| Verify the latest AV signatures are installed into the management console. | Version Used: ____________ |
| Expected Result to pass: |  |
| Verify the version of AV in Trellix console. |  |

Verify ePO Software Deployment

This task is to verify the versions of AV on each HMI/Server match the Trellix ePO in SP1:

Log into the SP1 using an administrator account and launch the Trellix ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “System Tree View -> Systems tab-> Preset: This Group and all Subgroups”. Click on the name of the HMI/Server to verify and choose the “Products” tab.

A list of the products and the version of each will be listed.

Now login into the HMI/Server. In the bottom right in the task bar, a Trellix icon should be present.

Right click on the Trellix icon and click “About”. A list of all the products installed will appear. Verify the versions match the ePO console Products tab for Trellix Data Exchange Layer, Trellix Application Control, Trellix Agent and Trellix DLP Endpoint.

Right click on the Trellix icon and click “Trellix Endpoint Security -> About”. A list of all the products installed will appear. Verify the versions match the ePO console -> Products tab for Endpoint Security Platform and Threat Prevention.

| Description | Comments & Observations |
| --- | --- |
| Verify all machines are up to date with management console. Check locally each HMI has the same definition level as management console. |  |
| Expected Result to pass: |  |
| Verify the version of AV matches from HMI/Servers to the ePO console. |  |

Verify Antivirus Software Operation

This task is to verify viruses that are being detected by the HMI/Server and Trellix ePO in SP1 and they can be removed from the system:

Log into an HMI/Server using an administrator account. Open file explorer and type this path: \\ca1\Admin_Procedures\OTArmor. Locate the “Test-Antivirus” and copy it into the desktop of the HMI/Server to be tested.

Right click on “Test-Antivirus” and choose “Run with Powershell”. Once the Powershell was run a pop up should appear from Trellix stating a virus was detected.

- Note: If the system has Solidcore installed, it will be necessary to add the powershell script to Solidcore rules to be allowed to run in “Enabled” mode.

Log into the SP1 server using an administrator account and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “Tree View -> System tab-> Preset: This Group and all Subgroups”. Click on the name of the HMI/Server to verify and choose the “Threat Events” tab.

A list of threat will be presented, select the one generated as part of the testing and click on “Actions -> Delete”.

| Description | Comments & Observations |
| --- | --- |
| Apply a test virus to an HMI. Verify is detected on the HMI, in the Trellix Management Console. |  |
| Expected Result to pass: |  |
| Verify the virus is detected by Trellix in the HMI/Server and ePO. |  |

Verify Threat Event on LM1 (optional)

Log into the LM1 server using an administrator account and launch the Splunk web management interface shortcut on the desktop.

Select “OTArmor Visability” in the menu.

Select “Endpoint Protection”.

Verify that the “Antivirus Events” counter increments.

Click on the “Antivirus Events” number and verify the “Antivirus Event Detail” displays the threat event that was generated in the previous section.

| Description | Comments & Observations |
| --- | --- |
| Apply a test virus to an HMI. Verify the threat event is displayed in the “Nexus OTArmor – Visibility” console. |  |
| Expected Result to pass: |  |
| Verify the threat event is detected is displayed in the Visibility console. |  |

Verify Device Control Policy

This task is to verify a policy that exists to control USB Devices in Trellix ePO in SP1:

Log into the SP1 using an administrator account and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “Menu -> Policy Catalog ->Data Loss Prevention x.x ”. Verify the DLP Policy “GEV Block All Devices” exists.

| Description | Comments & Observations |
| --- | --- |
| Verify there is a device control policy that closes USB ports. |  |
| Expected Result to pass: |  |
| Verify the policy exists in ePO Applied to HMI’s & OTArmor server which are subgroups under system tree. |  |

Verify USB Device Access

This task is to verify you can access USB devices in HMI/Server with the correct user account:

Log into an HMI/Server using the “admin” account. Insert any encrypted USB to be tested.

Verify under this account you can access the USB and its contents.

| Description | Comments & Observations |
| --- | --- |
| Verify USB devices can be accessed when an HMI/Server logs in with the exception user account. | HMI Tested: _____________ |
| Expected Result to pass: |  |
| Verify access to USB devices is available for the exception user Account. |  |

Verify USB Device Restrictions

This task is to verify access to USB devices is restricted for users without authorization:

Log into an HMI using the “GEMaint” account. Insert an encrypted USB to be tested.

Under this account, a pop up should appear explaining DLP has blocked the device.

Attempt to access files on the device and verify an “Access Denied” message is received when trying to get the USB’s contents.

Log into the SP1 server using an administrator account and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to Menu -> Policy Catalog -> Data Loss Prevention 11.X -> under policy - GEV Block All Devices”. Select “Edit -> GEV Removable Storage Device Rule -> Device Control -> GEV Block Removable Device Rule, choose “Exceptions” tab and choose “Excluded Users”. Verify that the GEMaint account does not have a USB exception.

| Description | Comments & Observations |
| --- | --- |
| Verify USB devices can NOT be accessed when an HMI logs in with a different user account from the exception. |  |
| Expected Result to pass: |  |
| Verify there’s NOT access to USB devices with the incorrect exception User Account. |  |

Verify USB Device Restrictions Event on LM1 (Optional)

Log into the SP1 server using an administrator account and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “Menu -> Automation -> Server Tasks”.

Select “Run” on the “DLP Block Events” task.

Verify the “DLP Block Events” task status is “Completed”.

Log into the LM1 server using an administrator account and launch the Splunk web management interface shortcut on the desktop.

Select “OTArmor Visability” in the menu.

Select “Endpoint Protection”.

Verify that the “DLP” counter increments.

Click on the “DLP Events” number and verify the “DLP Event Detail” displays the USB block event that was generated in the previous section.

| Description | Comments & Observations |
| --- | --- |
| Verify the USB Device Restriction event is displayed in the “Nexus OTArmor – Visibility” console. |  |
| Expected Result to pass: |  |
| Verify the USB Device Restriction is detected displayed in the Visibility console. |  |

SolidCore

This task is to verify SolidCore is working properly.

Changing Status

Log into each HMI/Server with an administrator account.

Open an administrator command prompt and verify the system is solidified, in enable mode, in lock down mode and is managed by the ePO server

Log into the SP1 with administrator credentials and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “System Tree”, click on “My Organization” and select all the devices listed and under “Actions” select “Agent”-> “Run Client Task Now”. A new screen will show up, on the left pane select “SolidCore 8.X.X”. At the middle pane select “Begin Update Mode”. At the right pane select “Create new task” and click on “Run Task Now”.

Wait until the task completes.

On HMI/Server, open an administrator command prompt and verify the system is in Update mode.

Repeat steps to change into different modes

Switching between modes

From Observe mode, you can switch to Enabled or Disabled mode.

From Enabled mode, you can switch to Disabled, Update, or Observe mode.

From Update mode, you can switch to Enabled or Disabled mode.

From Disabled mode, you can switch to Enabled, Update, or Observe mode.

| Description | Comments & Observations |
| --- | --- |
| Verify the change on the mode status is working. |  |
| Expected Result to pass: |  |
| Verify change of status executes successfully. |  |

Testing SolidCore Application

Log into the DR1 Server with an administrator account.

Open an administrator command prompt and verify the system is solidified, in enable mode, in lock down mode, and is managed by the ePO server.

Locate the “putty.exe” file and copy the application to a HMI’s desktop.

On the HMI, open an administrator command prompt and verify the HMI is solidified, in enable mode, in lock down mode, and is managed by the ePO server.

Attempt to execute the putty application on the desktop. Verify that the application is blocked by whitelisting.

From the ePO server, place the HMI in update mode.

Verify the HMI is in update mode. Erase and copy Putty again and attempt to run the application on the desktop. Verify the file is permitted to be executed.

From the ePO server, remove the system from update mode to enable mode. Verify the HMI that it is in enable mode.

Attempt to execute the Putty application on the desktop, verify that the application is permitted to execute.

| Description | Comments & Observations |
| --- | --- |
| Verify Putty cannot be run unless in update mode. |  |
| Expected Result to pass: |  |
| Verify running Putty gets denied by solidcore and allows it when in update mode. |  |

SIEM (Optional)

The following test items are designed to verify functionality and configuration of the Security Incident     and Event Monitoring (SIEM) capabilities provided by the security appliance.

SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards

Demonstrate the following widgets displayed on the GE Default dashboard & are populated with event data:

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

In view “GE Dashboard” consists of below events.

Windows Device Events.

Network Device Events.

VMware Device Events.

Events count by Host

Events

Failed Login by user.

Open the NERC-CIP 002 Dashboard and confirm the widgets are populating with event data

| Description | Comments & Observations |
| --- | --- |
| - Verify GE Default dashboard & are populated with event data: - Windows Device Events - Network Device Events - VMWare Device Events - Event Summary - Event count by Host - Events - Failed Login by User - NERC-CIP 002 Dashboard |  |
| Expected Result to pass: |  |
| Verify all the devices events are populated in GE Default SEM dashboard. |  |

Verify Asset Listing

Verify that all applicable assets are listed in the Trellix SIEM appliance, and are populated within their respective Asset Groups

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

From the ESM Dashboard menu, Select Asset Manager.

In Asset Manager click on Asset tab you can see the list of Asset Groups as defined below.

VMware

Windows

Network devices

Non-Windows

| Description | Comments & Observations |
| --- | --- |
| Verify all Devices are added in Asset Groups as defined below. - VMware - Windows - Network devices - Non-Windows |  |
| Expected Result to pass: |  |
| Verify all the devices are listed in Asset groups. |  |

Verify Data Sources in Local Receiver – ELM.

Verify that all applicable data sources are listed in the Trellix SIEM appliance, and the correct properties are assigned to each one.

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

From the ESM Dashboard menu, Select ELM Search.

From the Configuration tab, select Local Receiver-ELM and click Properties ()

In the receiver /ELM Properties – Local Receiver – ELM windows, select Data sources and verify all Devices are added in Data sources list.

| Description | Comments & Observations |
| --- | --- |
| Verify that all devices’ data sources are listed in the Trellix SIEM appliance, and the correct properties are assigned to each one. |  |
| Expected Result to pass: |  |
| Verify all the devices are listed in the Data sources list |  |

Verify Event Logging

Verify that an event is displayed in the Windows Login Events widget of the GE Default Dashboard after a successful or invalid login attempt.

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

In view “GE Dashboard” we can see windows login events.

| Description | Comments & Observations |
| --- | --- |
| Verify that an event is displayed in the Windows Login Events widget of the GE Default Dashboard after a successful or invalid login attempt. |  |
| Expected Result to pass: |  |
| Verify all windows login events are displayed in Windows login events Widget. |  |

SIEM Report Generation

Verify that a selected report can be generated and contains relevant event data

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

From the ESM dashboard menu, select System properties

In the system properties tree, select Reports and click on add and generate report.

Click on files, and in the files, list select file and click on download the report.

| Description | Comments & Observations |
| --- | --- |
| Verify that a selected report can be generated and contains relevant event data. . |  |
| Expected Result to pass: |  |
| Verify that a selected report can be generated and downloaded successfully. |  |

Trend Micro (Optional)

Verify Security Agent and Policy Status

This task is to verify the Security Agents are phoning home to the Apex One and Apex Central console and verify the Security Agent Policies are correct.

Login to the SP3 Server with admin credentials.

Double-click the “Trend Micro Apex One” desktop shortcut.

Login to the console with admin credentials, select Domain Name.

Select the “Agents” tab -> select “Agent Management”.

In the Agent Tree -> under Apex One Server -> select the HMI domain.

Verify the endpoint(s) are in the list and verify the connection status is “Online”.

Close the Apex One console.

Login into SP2 with Admin credentials.

Double-click the “Trend Micro Apex Central” desktop shortcut.

Login to the console -> select “Log on with Domain Credentials”.

Select the “Policies” tab -> click “Policy Management”.

Click the “product” drop-down and select “Apex One Security Agent”.

In the policies table -> navigate to the “Deployed” column.

Click the hyperlinked number next to the “Nexus Workstation Security Policy” and verify the endpoints.

Scroll over and verify under the “Description” column that all the components are “Deployed”.

Close the window.

On the “Policy Management” page -> click the hyperlinked number next to the “Nexus Server Security Agent Policy” and verify the endpoints.

Scroll over and verify under the “Description” column that all the components are “Deployed”.

Close the window.

In the policies table -> verify there are no “Offline” agents (there will be a hyperlinked number if so)

| Description | Comments & Observations |
| --- | --- |
| Verify all HMIs and Security machines are reporting in the SP2/3 Console. |  |
| Expected Result to pass: |  |
| Verify all the devices are listed in the SP2/3 console. |  |

Verify Pattern Update

Login to the SP2 Server.

Double-click the “Trend Micro Apex Central” desktop shortcut.

Login to the console -> select “Log on with Domain Credentials”.

Navigate to “Administration -> Updates -> Manual Update”.

Verify that in “Components” -> “Products (All managed products and Apex Central)” is selected.

Verify that “Enable intelligent component downloading” is checked.

In “Update Source” -> select “Other update source” is selected.

Verify path is set to “C:\TM_Update” is set.

In “Deployment Plan” -> select “Do Not Deploy”.

Select "Save”.

Obtain the latest Trend Micro Pattern/Updates -> Copy the latest Trend Micro Apex Patterns/Updates to the “C:\TM_Update” folder.

Record the version of the Category - > Antivirus -> Virus Pattern under “Comments and Observations” below.

In the Manual Update window, select “Download Now”.

Wait for the “Manual Update” to complete.

Check that updates have been loaded.

Refresh the Apex Central Console (web page).

Record the version of the Category - > Antivirus -> Virus Pattern under “Comments & Observations” below.

Select “Save”.

| Description | Comments & Observations |
| --- | --- |
| Verify latest AV patterns are installed into the management console. |  |
| Expected Result to pass: |  |
| Verify the version of SP2 console is updated. |  |

Verify Update Endpoints

This task is to verify the versions of Pattern on each HMI/Server match the SP2 Server:

Select an endpoint to verify updates, record the name of the server/hmi under “Comments & Observations”.

Right-click on the Trend Micro icon in the task manager and select “component versions”

Record the Virus Pattern version under “Comments & Observations”.

Select “Close”.

Login to the SP2 Server.

Double-click the “Trend Micro Apex Central” desktop shortcut.

Login to the console -> select “Log on with Domain Credentials”.

Navigate to Directories -> Products.

Expand the product directories and select the Apex One server.

Select Tasks -> Deploy Pattern Updates -> Deploy Now.

Wait for the “Deploying patterns….” to complete.

Navigate to Administration -> Command Tracking.

The status of the “Deploy Pattern Updates” can be monitored.

The task will be completed when the number in the Successful column is a “1”.

Refresh must be selected; the screen does not auto update.

Verify the pattern has updated on the endpoint.

In the HMI/Server, right-click on the Trend Micro icon in the task manager and select “component versions”.

Record the new Virus Pattern version under “Comments & Observations.

| Description | Comments & Observations |
| --- | --- |
| Verify all machines are up to date with management console. Check locally each HMI has the same definition level as management console. |  |
| Expected Result to pass: |  |
| Verify the version of AV matches from HMI/Servers to the SP2 console. |  |

Verify AV Software Operation

This task is to verify viruses being detected by the HMI/Server and SP2 Server and they can be removed from the system:

Log into a server or workstation (with the Apex Security Agent) using the admin account. Record the name of the server under “Observation & Comments” below.

Create EICAR test file.

Open notepad as an administrator.

Type or paste in the following text:

- X5O!P%@AP[4\PZX54(P^)7CC)7}$EICAR-STANDARD-ANTIVIRUS-TEST-FILE!$H+H*

Save the file as eicar.com.

Verify the endpoint displays a “Threat/Violations Found” message.

Click on the detection count and verify that the threat has been quarantined.

Login to the SP2 Server.

Double-click the “Trend Micro Apex Central” desktop shortcut.

Login to the console -> select “Log on with Domain Credentials.

Navigate to Detections -> Logs -> Log Query.

Select “Virus/Malware detections”

Select “All products”

Select “Last 24 hours”

Select “Search” to display results.

- Note: It may take some time for the Virus/Malware indication to display in the log.

| Description | Comments & Observations |
| --- | --- |
| Apply a test virus to an HMI. Verify is detected on the HMI, in the SP2 Console. |  |
| Expected Result to pass: |  |
| Verify the virus is detected by SP2 in the HMI/Server and SP2 Console. |  |

Verify Device Control - USB Device Access

This task is to verify you can access USB devices in HMI/Server with the correct user account:

Log into a server or workstation (with the Apex Security Agent) using the admin account. Record the name of the server under “Comments & Observations”.

Plug-in/attach a USB storage device.

Navigate to the attached USB storage device and attempt to open a folder/file.

Verify the attempt is blocked (pop-up should appear).

Copy the “listDeviceInfo” application to the workstation.

Run the “listDeviceInfo” application as administrator.

Record the following information.

Vendor:	_____________

Model: _____________

Serial ID: ______________

Create a group in Active Directory called “Trend Micro Allow Removal Media” (if it is not already created).

Add a user to this group. This will be used for testing in later steps.

Record the username under “Comments & Observations”.

Login to the SP2 Server.

Double-click the “Trend Micro Apex Central” desktop shortcut.

Login to the console -> select “Log on with Domain Credentials”.

Click on the “Detections” tab -> select “Log – Log Query”.

In the drop-down -> select “Device Control violations”-> click “Search”.

- NOTE: Device Control events may take some time to appear in the log. Wait and recheck the query until the event(s) appears.

Verify the event details.

Add an “Allowed USB device”.

Select the Security Policy that will be used to add a trusted USB device.

Expand Device Control Settings

Select the “Internal Agents” tab.

Select “+ Add”.

Allowed Removal Drive Access Policy Configuration.

User Accounts: Trend Micro Allow Removal Media.

Floppy disks: List device content only and select “Block”

CD/DVD: List device content only and select “Block”.

Network Drives: Full Access

USB storage drives: List device content only and select “Block”.

Select the Allowed USB Devices button.

Enter the Vendor, Model and Serial ID of the USB device. Select “Full Access” and then select “OK”.

Select “Block the AutoRun function on USB devices.

Select “Display a notification….”.

Mobile Devices -> Storage: Block

Non-Storage Devices: Select “Block” for all devices except “COM and LPT ports”.

Select “OK”.

Repeat steps for External Agents.

Select “Deploy” to deploy Security Policy to endpoints.

Once deployment is complete verify that USB now works with the user that was selected and does not work for other users.

| Description | Comments & Observations |
| --- | --- |
| Verify USB devices can be accessed when an HMI/Server logs in with the exception user account. | HMI Tested: _____________ |
| Expected Result to pass: |  |
| Verify access to USB devices is available for the exception user Account. |  |

Application Control

This task is to verify Application Control is working properly.

Log into a server or workstation (with the Apex Security Agent) using the admin account.

Record the name of the server under “Comments & Observations”. Make sure the HMI/Server is not under any Patching Policy.

Navigate to “C:\Staples Usb\” on DR1. Copy it to the C Drive of the HMI/Server.

Double-click the “Staples Usb.exe” -> verify the application is blocked (Policy Violation pop-up should appear).

Login to the SP2 Server.

Double-click the “Trend Micro Apex Central” desktop shortcut.

Login to the console -> select “Log on with Domain Credentials.

Click on the “Detections” tab -> select “Log – Log Query”.

In the drop-down -> select “Application Control violations” -> click “OK” -> click “Search”.

Verify the event details.

- NOTE: Application Control events may take some time to appear in the log. Wait and recheck the query until the event(s) appears.

Export the application control violations to csv, by selecting “Export to CSV”.

Open the exported file and copy the SHA-256 hash value.

Create Putty Policy

Navigate to Policies -> Policy Resources -> Application Control Criteria.

Select “+ Add Criteria -> Allow”.

Allow Criteria Settings

Name: Allow Putty.

Trust Permission: Application cannot execute external processes.

Match Method: Hash Values.

Input Method: Manual.

Select “SHA-256”.

In the hash value field, paste the hash value from the csv export.

In the description field, enter “Putty”.

Select “Save”.

Navigate to Policies -> Policy Management.

Select either the Nexus Server Security Agent Policy or Nexus Workstation Security Agent Policy.

- Note: Select the policy that matches the system the event was generated on.

Expand the “Application Control Settings”.

Select “All user accounts”.

Assign Rule Settings

Select “Allow Putty” and verify it moves to the “Selected criteria” window.

Select “OK”.

Select “Deploy” to deploy policy to endpoints and wait for policy to be deployed.

Note the policy version of the policy that was deployed under “Observation & Comments” below.

Log into the endpoint where the application violation was generated.

Check policy version.

Right-click on the Trend Micro icon in the task bar and select “Component Versions”.

Verify that the Apex Central policy version matches the policy number noted in Apex Central.

- Note: Hover over the “I” at the end of the policy name to get version.

Verify that the blocked application now can run.

| Description | Comments & Observations |
| --- | --- |
| Verify Putty cannot be installed unless it is allowed. |  |
| Expected Result to pass: |  |
| Verify Putty installation gets denied by whitelisting and allows it when allowed in policy. |  |

Tripwire Industrial Visibility (Optional)

Verify Domain Integration

Log into Domain Controller and verify one user account has been created with the “TIV Administrators” group, and the second account with the “TIV Users” group.

Log into the DR1 Server and launch the TIV application.

Log into the application using the TIV Admin account assigned to the “TIV Administrators" group.

Verify the user has administrative rights to the TIV system.

Log out of the TIV console

Log into the application using the TIV User account assigned to the “TIV Users" group.

Verify the user does not have administrative rights to the TIV system.

| Description | Comments & Observations |
| --- | --- |
| Verify sign in with the TIV application has the correct domain user credentials and that the administrative rights are assigned to TIV Administrators and the TIV Users do not have administrative rights. |  |
| Expected Result to pass: |  |
| Successful sign-in to the TIV application with the correct domain user credentials. The TIV Administrative rights are assigned to “TIV Administrators” and the “TIV Users” do not have administrative rights. |  |

Verify Control Protocol Decoding

Launch the TIV application from the DR1 server.

Log into the application as an account with TIV Administrator Privileges

From an HMI or Engineering Workstation, go “Online” with the Mark VIe controller.

Perform a configuration download to the Mark VIe controller.

Observe that a pop-up warning is presented that detects the download of the Mark VIe controller.

Navigate to the “Alerts” menu and locate the controller download notification. Click into the details of the test signature.

Verify that the proper source and destination device are shown for the detected download activity.

| Description | Comments & Observations |
| --- | --- |
| Verify TIV application alerts on a Mark VIe Controller download and determines the source and destination of the download under administrative privileges. |  |
| Expected Result to pass: |  |
| The TIV application alerted on a Mark VIe Controller download and displayed the source and destination of the download under administrative privileges. |  |

Verify Malicious Signature Detection

Launch the TIV application from DR1.

Log into the TIV application as an account with TIV Administrator Privileges.

From the DR1, Open file explorer and type this path:\\CA1\Admin_Procedures\OTArmor. Locate the “Test-NIDS2.ps1” and copy it into the desktop and execute the Test-NIDS2.ps1 PowerShell targeting a remote system whose link is monitored by the AM1 server.

Observe that a pop-up warning is presented that detects the transmission of the test signature.

Navigate to the “Alerts” menu and locate the test signature. Click into the details of the test signature.

Verify that the proper source and destination device are shown for the detected signature activity.

From the DR1, Open file explorer and type this path:\\CA1\Admin_Procedures\OTArmor. Locate the “Test-Antivirus” and copy it into the desktop and execute the “Test-AntiVirus.ps1” PowerShell script.

Open a file share with a remote system whose connection is monitored by the AM1 server.

Copy the “Virus_Test.com” file to the remote system.

Observe that a pop-up warning is presented that detects the transmission of the test signature.

Navigate to the “Alerts” menu and locate the test signature. Click into the details of the test virus signature.

Verify that the proper source and destination device are shown for the detected signature activity.

| Description | Comments & Observations |
| --- | --- |
| Verify TIV application alerts on a Network Intrusion Detection and an Anti-Virus test. Verify the alert shows the proper source and destination of these tests. |  |
| Expected Result to pass: |  |
| The TIV application alerted both a Network Intrusion Detection and an Anti-Virus test. The alerts show both the proper source and destination of these tests. |  |

Verify Active Query Information

Launch the TIV application from DR1.

Log into the TIV application as an account with TIV Administrator Privileges.

Navigate to the “Assets” page.

Locate a Windows System discovered by the TIV application. Record the name of the selected system: _____________________

Locate a Cisco Switch discovered by the TIV application. Record the name of the selected switch: _____________________________

Select the checkbox next to the Windows system.

Click the “Assign/Unassign Queries” button

From the drop down select “GEV_WMI_Credentials” and click “Assign”

Select the check box next to the selected Cisco Switch.

Click the “Assign/Unassign Queries” button

From the drop down select “GEV_Cisco_Query” and click “Assign”

From the menu select “Configuration”, then “Active Detection”

Click the checkbox next to the GEV_WMI_Credentials and GEV_Cisco_Query.

Click the “play” button to run the queries

Confirm the queries complete successfully.

Navigate to the “Assets” page.

Locate the Windows device selected previously and click into the details for the device. Verify that information such as Operating System, Patches, and Installed software is displayed.

Locate the Cisco device previously selected and click into the details for the device. Verify that information such as Firmware and vulnerabilities is listed.

| Description | Comments & Observations |
| --- | --- |
| Verify the TIV application (under administrative privileges) can discover a Windows System (HMI) to detail the device’s current list of Operating System, Patches and Installed Software. Verify the TIV application (under administrative privileges) can discover a Cisco Switch to detail the devices current list of Firmware and Vulnerabilities. | HMI Tested: ___________________________ Cisco Switch Tested: ___________________________ |
| Expected Result to pass: |  |
| The TIV application (under administrative privileges) discovers a Windows System (HMI) and details the devices current list of Operating System, Patches and Installed Software. The TIV application (under administrative privileges) discovers a Cisco Switch and details the device’s current list of Firmware and Vulnerabilities. |  |

Controller Hardening

Secure Mode

This task is to verify the Mark VIe controllers can be put into Secure Mode.

In Toolbox, verify the Mark VIe controllers can be put into Secure Mode.

In CA1, verify the CA1 server is issuing a certificate for the controllers.

Remove controller from secure mode.

| Description | Comments & Observations |
| --- | --- |
| Verify the Mark VIe Controller can be put into Secure Mode. Ensure CA1 is issuing certificates for the controller. |  |
| Expected Result to pass: |  |
| Verify that the Mark VIe Controller can be put into Secure Mode, CA1 is issuing certificates for the controller. |  |

SPLUNK (Optional)

Verify Firewall Unsuccessful logins

If not generated previously, generate several failed logins to the firewall management web page.

Log into LM1 using an administrator account and launch the Splunk web management interface shortcut on the desktop.

Click “Search” on the menu. A window will show, click on “Data Summary”.

A window will pop up with all the devices sending logs to Splunk. Click the firewall device and look for “login failed" events.

| Description | Comments & Observations |
| --- | --- |
| Verify firewall reports to Splunk when unsuccessful login attempts are made as a troubleshooting tool. |  |
| Expected Result to pass: |  |
| Verify Splunk is receiving “login failed” logs from the firewall. |  |

Verify Devices are reporting to Splunk

Log into LM1 server using an administrator account and launch the Splunk web management interface shortcut on the desktop.

Click “Search” and then click on “Data Summary”.

A window will pop up with all the devices sending logs to Splunk:

- Servers, HMIs, Switches, Controllers, Firewalls and Hypervisors.

Verify all the devices listed are expected and there’s no devices missing. (Devices present and connected in the network). Also make sure we receive logs for each device and the time is current.

| Description | Comments & Observations |
| --- | --- |
| Verify all devices are reporting to Splunk. This includes all HMIs, Virtual machines, switches, and firewall. |  |
| Expected Result to pass: |  |
| Verify Splunk is receiving “logs” from the devices connected on the network successfully. |  |

Verify Successful/Unsuccessful login reporting

If not generated previously, generate several successful and failed logins on different devices logging to the Splunk.

Log into LM1 server using an administrator account and launch the Splunk web management interface shortcut on the desktop.

From the Splunk console -> select the GEV OTArmor™.

Verify the Controller panels are populated. The Windows Active Directory panel will alert on the following Windows event codes:

- Event code 4625: Login Failed

- Event code 4624: Login Success

| Description | Comments & Observations |
| --- | --- |
| Verify successful and unsuccessful login attempts are captured in the Splunk as a troubleshooting tool. |  |
| Expected Result to pass: |  |
| Verify Splunk is receiving “logon failure” and “logon success” from the devices connected on the network. |  |

Verify NIDS is reporting

    - If not generated previously, generate several NIDS strings in the system (Test-NIDS.ps1) on any of the HMIs and take note of the time they were executed. This powershell will simulate an attack in the system.

    - Log into the firewall and under Network->Interfaces check the port is configured for NIDS.

    - Also, under Log&Report->Intrusion Prevention, verify you got the logs for the attack (Test-NIDS.ps1).

    - Log into LM1 server using an administrator account and launch the Splunk web management interface shortcut on the desktop.

    - Click “Search & Reporting” and then on “Search” type “GEV NIDS TEST STRING”.

    - A list of logs will appear with the string on it. Make sure the times match with the ones you executed and from the devices they were executed.

| Description | Comments & Observations |
| --- | --- |
| Verify “GEV NIDS TEST STRING” can be found in the logs after executing Test-NIDS.ps1. |  |
| Expected Result to pass: |  |
| Verify Splunk is receiving “GEV NIDS TEST STRING” logs and they match the ones that were executed with Test-NIDS.ps1. |  |

- XONA (Optional)

Xona User Account Login

    - Log into the Internal Network Test PC as an administrator.

    - Open a Web Browser and access the Xona Login Page.

    - Login using User credentials.

    - Confirm that the user account only has access to connections they have been granted access.

    - Attempt to Launch an RDP connection to a Windows System.

    - Confirm the Connection Launches as expected.

    - Disconnect from the session.

    - Log out of the Xona platform.

| Description | Comments & Observations |
| --- | --- |
| Verify a connection is possible using User Credentials. |  |
| Expected Result to pass: |  |
| Verify connection is successfully possible with User Account. RDP connection is also possible. |  |

Xona Administrator Account Login

    - Log into the Internal Network Test PC as an administrator.

    - Open a Web Browser and access the Xona Login Page.

    - Login using Admin the following credentials.

    - Confirm that the Admin account has access to all Xona Menu options.

    - From the Menu select “LogsConnection History”

    - Locate the Session initiated 19.2.1.

    - Click on the “Process” button to process the video on the system, allow the processing to complete.

    - Click “View” and confirm that the recording of the session is played.

    - Close the csgadmin session.

| Description | Comments & Observations |
| --- | --- |
| Verify a connection is possible using Admin Credentials. |  |
| Expected Result to pass: |  |
| Verify connection is successfully possible with Admin Account. Verify recording session is possible. |  |

  - Xona File Transfer Test – SMB in SSL-VPN Tunnel

    - Log into the Test_Computer #1 Network Test PC as an administrator.

    - Open the FortiClient software using the shortcut on the users’ desktop, connect to the tunnel using the User credentials.

    - Open the Firefox Web Browser and access the Xona Login Page. The address for the Xona system under test is “https://10.0.2.10”.

    - Login using User credentials. This will be referred to as the User test session.

    - Open a Firefox Web Browser on the Baker Hughes network and connect to the Xona Platform. The address for the Xona system under test is “https://10.132.65.69”.

    - Login using the Admin credentials. This will be referred to as the Admin session.

    - Return to the internal Network Test PC and open a connection to the Xona SMB Share.

    - Attempt to upload the EICAR.txt test file, confirm that an error message is presented, and the file is not transferred to the SMB share.

    - Select another test file to transfer, record the name of the file uploaded to the Xona SMB Share: _______________

    - Return to the User Session and select the RDS Server Session.

    - From the “File Transfer” Menu, confirm the file exists in the drop-down box.

    - Select the file to be transferred and click the “Upload to CSG” button

    - Confirm a prompt is received that the file has been uploaded to the CSG.

    - Return to the Admin session, from the Menu select “User AdministrationFile Transfers”

    - Locate the file requested to be transferred and select “Approve”

    - Return to the User session and launch the connection to the RDS Server.

    - Once connected to the server, open the file transfer menu.

    - From the “Available Files” drop down, confirm the desired file is available for transfer.

    - Select the file from the drop-down menu, then click “Upload to Host”

    - From the host, select the file explorer and locate the remote drive “[drive letter] on Xona CSG”.

    - Open the “Download” folder and confirm the selected file is available.

    - Return to the Admin session, select the “User Administration—>File Transfer” menu. Click “Delete” to remove the files from the system.

    - Disconnect both sessions and close the VPN tunnel.

| Description | Comments & Observations |
| --- | --- |
| Verify a VPN connection is possible, and file transfer is possible. |  |
| Expected Result to pass: |  |
| Verify - Xona File Transfer Test – SMB in SSL-VPN Tunnel |  |

  - Xona File Transfer Test – Web Upload

    - Log into the Test_Computer #1 Network Test PC as an administrator.

    - Open the SSL-VPN Tunnel and connect to the tunnel using User credentials.

    - Open a Web Browser and access the Xona Login Page.

    - Login using User credentials. This will be referred to as the User test session.

    - Open a Web Browser on the Baker Hughes network and connect to the Xona Platform.

    - Login using the Admin credentials. This will be referred to as the Admin session.

    - Return to the User Session and select the RDS Server Session.

    - From the “File Transfer” Menu, click the “Browse…” option, under “Local Filesystem”.

    - Attempt to upload the EICAR.txt test file, confirm that the Xona shows a loading page, and never completes loading. Refresh the page and log back into the system and navigate to the test system again.

    - Select a different file to be transferred and record the name of the file.

    - Click the “Upload to CSG” button.

    - Confirm a prompt is received that the file has been uploaded to the CSG.

    - Return to the Admin session, from the Menu select “User AdministrationFile Transfers”.

    - Locate the file requested to be transferred and select “Approve”

    - Return to the User session and launch the connection to the RDS Server.

    - Once connected to the server, select the file transfer menu.

    - From the “Available Files” drop down, confirm the desired file available for transfer.

    - Select the file from the drop-down menu, then click “Upload to Host”.

    - From the host, select the file explorer and locate the remote drive “[drive letter] on Xona CSG”.

    - Open the “Download” folder and confirm the selected file is available.

    - Copy the file to the host system and confirm there are no errors.

    - Create a new text file on the desktop of the RDS system, name the file “Outbound Test”.

    - Open the file and add the following text: “This is a test of the outbound file transfer”. Save the changes to the file.

    - Copy the file from the desktop to the “[drive letter] on Xona CSG” folder. Leave the file in this root folder, do not copy the file into the “Download” folder.

    - Open the File Transfer menu and select “Download to CSG”

    - Confirm a prompt is received that the file has been downloaded.

    - Return to the Admin session, from the Menu select “User AdministrationFile Transfers”

    - Locate the file requested to be transferred and select “Approve”

    - Return to the User session, select the file transfer menu.

    - From the drop-down box under “Available Files”, locate the “Outbound Test” file. It may be necessary to click the “Refresh Files” button.

    - Once selected, click the “Download from CSG” button.

    - Confirm a pop-up is received, click the link to download the file.

    - Open the file and confirm it contains the desired text.

    - Return to the Admin session, select the “User Administration—>File Transfer” menu. Click “Delete” to remove the files from the system.

| Description | Comments & Observations |
| --- | --- |
| Verify a Xona File transfer is possible, and file transfer is possible. |  |
| Expected Result to pass: |  |
| Verify - Xona File Transfer Test – Web Upload. |  |

  - Xona Web Portal Access Test - SSH Session / SMB Upload

    - Log into the Test_Computer #2 Network Test PC as an administrator.

    - Open a Chrome Web Browser and access the Fortinet SSL-VPN web page using the following address:https://10.0.1.201:45000.(based on project ip subnet)

    - Login using the Web User credentials.

    - From the page presented, select the “Xona SMB” shortcut. Confirm a web page is presented with files.

    - Utilize the “Upload” button to submit a file to the SMB share, confirm the file appears in the share.

    - Close the window to the SMB share.

    - Return to the SSL-VPN web portal, launch the Xona shortcut.

    - Launch the connection to Xona.

    - Login using User credentials.

    - Launch the SSH connection to the cisco switch.

    - Confirm the session can be established and interacted with

    - Close the user session.

| Description | Comments & Observations |
| --- | --- |
| Verify a Xona Web Portal Access Test - SSH Session / SMB Upload. |  |
| Expected Result to pass: |  |
| Verify - Xona Web Portal Access Test - SSH Session / SMB Upload. |  |

  - Xona VNC Session Test

    - Log into the Internal Network Test PC as an administrator.

    - Open a Web Browser and access the Xona Login Page.

    - Login using User credentials. This will be referred to as the User test session.

    - Open a Web Browser on the Baker Hughes network and connect to the Xona Platform.

    - Login using the Admin credentials. This will be referred to as the Admin session.

    - From the CSG Admin Session, open a connection to the Server, confirm the VNC server is active on the test system.

    - Return to the User Session and select and Launch the VNC Server Session.

    - Confirm the VNC session establishes and the VNC session can interact with the System.

    - Disconnect and close both sessions.

| Description | Comments & Observations |
| --- | --- |
| Verify - Xona VNC Session Test. |  |
| Expected Result to pass: |  |
| Verify - Xona VNC Session Test. |  |

  - Xona Session Monitoring/Kill Test

    - Log into the Internal Network Test PC as an administrator.

    - Open a Web Browser and access the Xona Login Page.

    - Login using User credentials. This will be referred to as the User test session.

    - Open a Web Browser on the GEV network and connect to the Xona Platform.

    - Login using the Admin credentials. This will be referred to as the Admin session.

    - Return to the User Session and select any Server Session.

    - Launch the connection to that Server.

    - From the Admin session, navigate to the “UsersMonitor Connections” menu item.

    - Locate the session for the User and click “Monitor”.

    - From the screen that opens, select “Connect”

    - Confirm the system connects to the live user session.

    - Return to the User session and make some changes, confirm those changes are updated on the Admin session.

    - From the Admin session click “disconnect” and return to the “Monitor Connections” screen.

    - Click “Kill” next to the user session.

    - Confirm that the User session is closed

    - Attempt to log in with the User account, confirm that the account is locked out.

    - Return to the Admin session, unlock the User account.

    - Return to the User session and confirm the user can log in.

| Description | Comments & Observations |
| --- | --- |
| Verify - Xona Session Monitoring/Kill Test. |  |
| Expected Result to pass: |  |
| Verify - Xona Session Monitoring/Kill Test. |  |

  - FortiGate VPN Host Rejection Test

    - Log into the HMI #2 Network Test PC as an administrator.

    - Open the SSL-VPN Tunnel and connect to the tunnel using the User credentials.

    - Confirm the FortiClient blocks the system from connecting and provides a notice that the Anti-Virus is out of date.

| Description | Comments & Observations |
| --- | --- |
| Verify - FortiGate VPN Host Rejection Test. |  |
| Expected Result to pass: |  |
| Verify - FortiGate VPN Host Rejection Test. |  |

  - Xona Duration Testing

    - Log into the HMI #1 Network Test PC as an administrator.

    - Open the SSL-VPN Tunnel and connect to the tunnel using User credentials.

    - Open a Web Browser and access the Xona Login Page.

    - Login using the User credentials. This will be referred to as the User test session.

    - Open a session to any Server system. Minimize the virtual system, leaving the testing running.

    - Log into the HMI #2 Network Test PC as an administrator.

    - Open a Chrome Web Browser and access the Fortinet SSL-VPN web page using the following address:https://X.X.X.X:45000. Where X is the IP for the device.

    - Login using the Web User credentials.

    - Open a session to Server system. Minimize the virtual system, leaving the testing running.

    - Leave the system running for 6 hours, return and confirm the user sessions are still active.

    - Close the user sessions.

| Description | Comments & Observations |
| --- | --- |
| Verify - Xona Duration Testing. |  |
| Expected Result to pass: |  |
| - Xona Duration Testing. |  |

- HIGH AVAILABILITY FAIL-OVER

    - Verify VH1, VH2 and VH3 are running. All VM’s on each hypervisor must be on and operating normally (Skyline Health good and make sure unhealth items in VSAN health).

    - Remove the HA Network connections from one of the Hypervisors (VH1 or VH2 or VH3).

    - Login into VSphere with admin credentials. Verify all the Virtual Machines associated with the Hypervisor chosen are migrating to their corresponding backup Hypervisors.

- Note. This step takes time, the change is not instant.

    - Reconnect the Network connections on Hypervisor chosen on step 20.1.2.

    - Manually migrate all the Virtual machines that belong the chosen Hypervisor:

      - Right click on the VM, select “Edit Settings” and Uncheck the CD Drive. Click “Save”.

      - Right click on the VM, select “Migrate” ->” Computer Resources” ->” Next”->” Finish”.

    - Verify the migration of the VM’s involved have been successful.

| Description | Comments & Observations |
| --- | --- |
| Verify the Virtual Machines associated with VHx move to its corresponding backup server. Return the network connections to VHx and manually migrate the VM’s to their original Virtual Host. Verify the migration is executed successfully. |  |
| Expected Result to pass: |  |
| Verify HA fail-over is performed successfully. All VMs migrate to the rest of the Hypervisors. Verify after re-establishing, that all VM’s can be migrated to their original Hypervisor. |  |

AGREED RESIDUAL ACTIONS

Description:

Identify residual actions, questions, agreements, or any other issues to be addressed after the CWT but before installation starts. Include who will be doing the work and the estimated completion date.  Additional residual action lists may be attached at the end of this document as needed.

| Item # | Description of Change or Action | Action Item Owner | Estimated Completion Date |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |
| 9 |  |  |  |
| 10 |  |  |  |
| 11 |  |  |  |

| GEV Approval | Date: _________ | Initials________ |
| --- | --- | --- |
| Customer Approval | Date: _________ | Initials________ |

CUSTOMER WITNESS TEST SIGNATURE SHEET

The undersigned agree that the factory acceptance test was completed on the date indicated.

GEV	CUSTOMER

Approval	Approval

___________________________________	___________________________________

(signature)	(signature)

______________	______________

(date)	(date)

GEV CONTROL SOLUTIONS

For

<CUSTOMER>

<SITE NAME>

<PROJECT NUMBER>

CUSTOMER WITNESS TEST

The following approvals constitute the satisfactory completion of the Customer Witness Test (CWT).

The CWT was conducted on a structured basis as outlined in the previous pages.

The above signatures constitute an agreement on the outstanding residual actions and a commitment by GEV to resolve and/or complete any outstanding action items.  Outstanding items are identified on the Agreed Residual Action Items list or as an attachment to this document.

Customer’s acceptance authorizes the billing associated with the Customer Witness Test completion.