THIRD ANGLE PROJECTION

THIS DRAWING TO BE REVISED IN MICROSOFT WORD ONLY.  THE SOURCE FILE IS STORED IN THE PLM

CYBER SECURITY

| LIST OF COMPLEMENTARY DOCUMENTS |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | DWG. NO. |
| 1 | Network Topology | 122T7871 |

TABLE OF CONTENTS

1.0	INTRODUCTION	4

1.1	Punch List Tabulation of Problem Reports	4

1.2	Error Correction / Retest	4

1.3	Change Management	5

1.4	Reference Documents	5

1.5	OTArmor Machine Roles	5

2.0	REQUISITION INFORMATION	6

3.0	AGENDA	6

Day 1 – 8:00AM to 4:00PM	6

	Steps 1 to 6	6

Day 2 – 8:00AM to 4:00PM	6

	Steps 7 to 12	6

Day 3 – 8:00AM to 4:00PM	6

	Steps 13 to 18	6

4.0	EQUIPMENT INSPECTION	7

4.1	Equipment Inspection	7

4.2	Remote Desktop to HMIs (Virtual machines only)	8

5.0	RADIUS	9

5.1	RADIUS Functionality	9

5.2	Verify RADIUS Account Login	11

5.3	Verify RADIUS Account Lockout	12

6.0	FIREWALL TESTING	13

6.1	Certificate Validation Use of HTTPS	13

6.2	Approved Use Banner	14

6.3	Firewall Backup and Restore	15

6.4	Verify NIDS Configuration	16

7.0	Cat Tools	17

7.1	Verify Network Switch is configured in CatTools	17

7.2	Verify Network Switch Backup Task in CatTools	18

7.3	Verify Configuration Changes are Identified	19

7.4	Verify the Network Switches can be restored using CatTools	20

7.5	Verify Network Switches have a customer approved banner during sign in (Optional)	21

7.6	Verify the Network Switches are synced to NTP source	22

7.7	Verify the Network Switches have a MAC address filter (Optional) (This is commercial offering only)	23

7.8	Disable any Unused Ports (Optional) based on the project scope this may be executed at the time of COD.	24

8.0	NTP	25

8.1	Verify NTP Synchronization	25

8.2	Verify Servers Sync to NTP Server (HMI’s Excluded)	26

9.0	Account Management	27

9.1	Default/Domain Accounts	27

9.2	Verify Operator Account	28

9.3	Verify Engineer/Maintenance Account	29

9.4	Verify Shared Accounts	30

9.5	Service Accounts	31

9.6	Verify Service Account Restrictions	32

9.7	Verify Service Account Password Policy	33

9.8	Domain Password Policy Settings	34

9.9	Verify Password Policy on Domain Accounts	35

9.10	Verify Password Policy on Local Accounts	36

9.11	Account Lockout	37

9.12	Verify Account Reset after Lockout	38

10.0	Windows Patching	39

10.1	Patch Scan and Deployment	39

10.2	Verify Device Detection for Patching	40

10.3	Verify Patch Deployment	41

11.0	HMI Backup & Restore	42

11.1	Perform Backups	42

11.2	Verify Restore Activities for Files/Folders.	43

11.3	Verify Restore Activities for Thick HMIs.	44

11.4	Verify System After Restore.	45

12.0	NETWORK SECURITY MONITORING	46

12.1	Monitoring Port	46

12.2	Nozomi Dashboard	47

12.3	Network Traffic Validation	48

12.4	Passive Monitoring and Network modeling and visualization Operation	49

12.5	Learning Mode Configuration	51

12.6	Malicious Signature detection	52

13.0	TRELLIX	53

13.1	Trellix Agent	53

13.2	Verify ePO Virus Definitions	54

13.3	Verify ePO Software Deployment	55

13.4	Verify Antivirus Software Operation	56

13.5	Verify USB Device Restrictions	57

13.6	SolidCore	58

13.7	Testing SolidCore Application	59

14.0	SIEM	60

14.1	SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards	60

14.2	Verify Asset Listing	61

14.3	Verify Data Sources in Local Receiver – ELM.	62

14.4	Verify Event Logging	63

14.5	SIEM Report Generation	64

15.0	Controller Hardening	65

15.1	Secure Mode	65

16.0	HIGH AVAILABILITY FAIL-OVER	66

17.0	AGREED RESIDUAL ACTIONS	67

18.0	CUSTOMER WITNESS TEST SIGNATURE SHEET	68

INTRODUCTION

This document describes the proposed Customer witness test (CWT) of the Cyber Security Management System.

The Customer witness test will take place in GE Vernova Facilities, during a period of 3 days. Testing will include hardware, software, and a documentation review of the system.  The intent of the test is to demonstrate that the system under test operates as designed. This document will be used as the approval document to provide a record of the test activities.

At the end of the CWT a summary of the test results and corrective actions will be added to this document and archived. Any items that cannot be resolved prior to shipment will be addressed by engineering and communicated to the site installation team prior to the unit outage by the most effective means possible.

Punch List Tabulation of Problem Reports

During the CWT test personnel will document any problems that require corrective action. The tester will identify their name, the date that the problem was found, any document references, and a description of the problem.

When problems are discovered, they will be reviewed with the engineer for that area. Problems and non-conformances shall be formally logged in Section  AGREED RESIDUAL ACTIONS.

The CWT owner or an engineer/technician under the direction of the CWT owner will implement all corrections. Problems will be considered resolved only when the engineer responsible for that area of the test signs them off. All problem reports must be resolved prior to authorization for shipment.

Error Correction / Retest

The timing of error corrections and retests will depend on the type and scope of the problems encountered. Problems that can be easily corrected will be corrected when identified and recorded in Section AGREED RESIDUAL ACTIONS. Problems that require more time to correct may be resolved and/or re-tested prior to shipment or as agreed between the parties.  Residual Actions may be moved to a Project Open Items List as a method of resolution as to not hold up completion of testing or shipment.

Replacement of any hardware, firmware or changes to the software configurations may require that the affected components or code be retested to ensure that the design remains valid as determined by the Test Engineer.  The retest will be performed using the relevant sections of this CWT procedure.

Change Management

A change management log will be used for the duration of the CWT. His log will track any changes made to the system that vary from the original configuration. All changes need to be approved by GEV and the customer. Logs will be recorded in the “Comments and Observations” of each task.

Reference Documents

The following is a list of reference documents used in conjunction with the Customer witness test the latest revisions of these documents will be used at the time of the test. The GE Cyber Engineer shall be responsible for obtaining the latest revisions.

- Network Topology (<122T7871>).

- GEV Controls Ports and Services Document (132M6452).

- Pre-CWT Ports and Services Scan Results.

Note: This document is a complete checklist for security features.  A project CWT checklist will be generated for the features included with a specific project."

OTArmor Machine Roles

1.5.1 OTDC1, OTDC2:

Primary and Secondary Domain Controllers. These machines manage authentication and configurations for other assets.

1.5.2 OTCA1:

Certificate Authority. This machine does a thing.

1.5.2 OTDR1:

Disaster Recovery. This machine hosts the CatTools and Acronis applications, which are used for backups and recovery.

1.5.3 OTPM1:

Patch Management. This machine hosts the Ivanti application, which is used for deploying Windows patches.

1.5.4 OTSP1:

System Protection. This machine hosts the Trellix Electronic Policy Orchestrator (ePO). The ePO is an agent-based software that manages Endpoint Security (Antivirus), SolidCore (Application Whitelisting) and DLP (Data Loss Prevention).

1.5.5 OTSIEM:

Security Information and Event Management. A Trellix non-Windows machine that is accessed via a web browser. OTArmor assets are configured to forward event logs to be centrally viewed and managed.

REQUISITION INFORMATION

Customer:   	< FPL OKEECHOBEE CEC >

End User:   	< Florida Power and Light company >

Site Name:	< OKEECHOBEE CEC >

Project number #: F7505G18>

GEV Control Personnel: <Torres, Elias>

AGENDA

| Day 1: 8:00AM – 4:00PM | Block 1 and Block 2 HMI Procedures |
| --- | --- |
| Day 2: 8:00AM – 4:00PM | Block 2 HMI and OTArmor Procedures |
| Day 3: 8:00AM – 4:00PM | OTArmor Procedure |

EQUIPMENT INSPECTION

This section applies only to the OTArmor DMZ.

The following sections provide a brief description of the inspection / test. It also permits the recording of comments and allows sign off on each test.

Equipment Inspection

This task performs a visual inspection system or HMIs.

| Description | Comments & Observations |
| --- | --- |
| Perform a visual inspection of the system or HMIs. |  |
| Expected Result to pass: |  |
| All components are present and represented in the system drawings. |  |

Remote Desktop to HMIs (Virtual machines only)

This task defines if the HMIs will need to have Remote Access enabled. If the HMI’s to be installed at site are not present during the CWT, this task will be performed at site.

If the HMIs are present during the CWT and Remote desktop access is requested, in each HMI:

Navigate to “Control Panel -> System -> Remote Settings”.

Select “Allow remote connections to this computer”.

If possible, select “Allow connections only from computers running Remote Desktop with Network Level Authentication (recommended)”. There may be cases when connecting to an older computer may need to leave this unchecked.

The following services must be turned on for remote desktops to work:

Navigate to “Control Panel -> Administrative Tools -> Services”.

Find the “Remote Desktop Services Service”, enable it and place it in automatic.

Find the “Remote Desktop Services User Mode Port Redirector”, enable it and place it in automatic. Start this service.

Verify Remote Desktop is added in the Windows Firewall:

Navigate to “Control Panel -> Windows Firewall -> Allow an app or feature through Windows Firewall”.

On the list displayed look for “Remote Desktop” and make sure “Domain” and “Private” are checked. If not, proceed to click on “Change Settings” and check “Domain” and “Private” and click “OK”.

Verify that RDP connections are successful.

NOTE. If RDP is not required by the customer or not needed anymore, disable Remote Desktop in the Windows Firewall.

| Description | Comments & Observations |
| --- | --- |
| If required, verify Remote Desktop is enabled on all HMIs. |  |
| Expected Result to pass: |  |
| Verify we can Remote Desktop into the HMI’s configured. |  |

RADIUS

RADIUS Functionality

This task is to verify the network switches that have been entered in Radius, this test will be performed on the DMZ Domain Controllers:

Log into one of the DCs using an administrator account and Launch the Server manager, open “Tools->Network Policy Server”.

Expand “RADIUS Clients and Servers” and select “RADIUS Clients” and verify the Network Switch are present as per Network Topology.

Disable the Network Policy Server on Domains.

Attempt to authenticate to a Network Switch from every network segment (block 1, block 2, DMZ) from DR1 using PuTTY, verify that the radius services can NOT successfully authenticate the “GESwitch & GEswitchOper” account.

Attempt to log onto a Network Switch from every network segment (block 1, block 2, DMZ) using the local account ‘Admin’ and verify it is successful.

Enable the Network Policy Server on Domains.

Attempt to authenticate to a Network Switch from every network segment (block 1, block 2, DMZ) from DR1 using PuTTY, verify that the radius services can successfully authenticate the “GESwitch & GEswitchOper” account.

Attempt to log onto a Network Switch from every network segment (block 1, block 2, DMZ) using the local account ‘Admin’ and verify it is unsuccessful

| Description | Comments & Observations |
| --- | --- |
| Review RADIUS in Active Directory on the DMZ Domain Servers to verify Network Switch is entered. When “Network Policy Server” is Disable verify: - Unsuccessful access occurs with “GESwitch & GEswitchOper” when trying to login into Network Switch. - Successful access occurs with Local “Admin” Account when trying to login into Network Switch. When “Network Policy Server” is started, verify: - Unsuccessful access occurs with Local “Admin” when trying to login into Network Switch. - Successful access occurs with “GESwitch & GEswitchOper” Account when trying to login into Network Switch. |  |
| Expected Result to pass: |  |
| - Confirm DMZ Domain Servers have the Network Switch(es) configured in Radius. - Confirm you can authenticate with the GESwitch & GEswitchOper user account in the Network Switch when the Network Policy Server is running. Confirm authentication fails when the Network Policy Server is NOT running. - Confirm you can authenticate with the Local Admin user account in the Network Switch when the Network Policy Server is NOT running. Confirm authentication fails when the Network Policy Server is running. |  |

Verify RADIUS Account Lockout

This task is to verify if a domain account will be locked after 10 failed attempts using RADIUS:

Log into the DR1 using an administrator account and launch the putty shortcut on the desktop, Provide IP address/Hostname details for a network switch and click on ok to open session.

Enter the correct Username but an incorrect password for the GESwitch & GEswitchOper account. Make sure you try these 10 times. (If Putty shows an error, please close Putty and open again).

After 10 tries, type the correct password. It should still report you are not able to log into the system.

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers”. Look for GESwitch & GEswitchOper Account and double click it.

Click on the “Account” tab, you will see the account is being locked. Check “Unlock Account” and click OK.

Try to login into a Network Switch using Putty with the correct Credentials and password. Confirm the account can login successfully.

| Description | Comments & Observations |
| --- | --- |
| Verify the GESwitch & GEswitchOper account is locked when entering 10 bad passwords. Reset the account, log in successfully. |  |
| Expected Result to pass: |  |
| Verify Account locks after 10 failed attempts. Also verify you can login successfully after resetting the account. |  |

- FIREWALL TESTING

  - Certificate Validation Use of HTTPS

This task is to verify that a firewall from each network segment (block 1, block 2, DMZ) can be connected using HTTPS vs HTTP:

    - Open Chrome from DR1 Server. In the browser type: “https://<name of firewall or IP Address> <enter>. Confirm you are prompted to log into the firewall.

    - Open another tab in Chrome and in the browser type: “https://<name of firewall or IP Address> <enter>. Confirm the page does not load.

    - Open CLI and execute the command below to verify certificate validity.

- diagnose sol certificate list

| Description | Comments & Observations |
| --- | --- |
| Verify the firewall is accessed using HTTPS and verify ssl certificate |  |
| Expected Result to pass: |  |
| Verify access is possible using HTTPS and found valid certificate. |  |

  - Approved Use Banner

This task is to verify the right banner that has been applied into a firewall from each network segment (block 1, block 2, DMZ). Banner should have been provided by the client. If a banner is not provided, this test will verify that a banner can be displayed:

    - Open Chrome from DR1. In the browser type: “https://<name of firewall or IP Address>” <enter>.

    - A banner should be shown before you are able to login into the system.

| Description | Comments & Observations |
| --- | --- |
| Verify proper banner is displayed when attempting to log into the firewall. |  |
| Expected Result to pass: |  |
| Verify the banner is presented before being permitted to login into the firewall. (Only if banner was given by client). |  |

  - Firewall Backup and Restore

This task is to verify a firewall from each network segment (block 1, block 2, DMZ) can be backed up and restored from a previous backup.

Backup:

    - Log into the DR1 using an administrator account and launch the kiwi CatTools application.

    - Execute a backup task for the Fortinet in the “Activities” tab.

    - Verify that the task completes successfully, and a current backup file is obtained.

    - Verify a scheduled task exists to perform a backup of the Fortinet device in the validation lab.

Restore:

    - Log into the DR1 using an administrator account and launch the Firewall shortcut on the desktop / open browser and type: “https://<name of firewall or IP Address>” <enter>. .

    - Modify the host name of the firewall to be something other than the current name.

    - Click the user (Top right) -> Configuration -> Restore.

    - Make sure we restore from “Local PC”, under File click on “+Upload”. Browse where we have the backup we want to restore with.  Leave password in blank and click ok.

    - Verify the restore has been done successfully by confirming the firewall has the proper hostname.

| Description | Comments & Observations |
| --- | --- |
| Verify firewall can be backed up using CatTools and restored from the firewall GUI. |  |
| Expected Result to pass: |  |
| Verify the backup file has been generated successfully and it can be accessed. Verify the restore has been deployed successfully. |  |

- Cat Tools

Cat Tools should be configured for network devices from all network segments

Verify Network Switch is configured in CatTools

This task is to verify Network Switch configured in CatTools:

Log into the DR1 using an administrator account and launch the CatTools shortcut on the desktop.

On the left panel you, under the “Devices” tab, a list of devices will be listed. Please verify the Network Switch is listed with its correct IP Address.

| Description | Comments & Observations |
| --- | --- |
| Verify the network switch is listed in CatTools. |  |
| Expected Result to pass: |  |
| In the list of devices, the network switch(es) will be present with correct IP Address(es). |  |

Verify Network Switch Backup Task in CatTools

This task is to verify network switch can be backed up using CatTools:

Log into the DR1 using an administrator account and launch the CatTools shortcut on the desktop.

On the right Panel, under “Activities” Tab, look for the “Backup Activity”.

Right click on the task and choose “Run Now”.

On the bottom panel, you will see and “Activity Log”, it will inform you how the activity is running and if it founds any error while executing. (Please be patient, getting a backup can take up to 5 to 10 minutes). Once the task is finished, the logs will report if the task is finished successfully or with errors.

When task finishes running successfully, go to the “File Explorer” and browse to the following path: “C:\Backups\Switches\Config”. It should list a file with the name “Config.Current.Running. [Name of Network Switch].txt”.

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switch(es) can be backed up in CatTools. |  |
| Expected Result to pass: |  |
| Backup tasks will run successfully, and a file will be created under C:\Backups\Switches. |  |

Verify Configuration Changes are Identified

This task is to verify Network Switch changes can be tracked using CatTools:

Log into DR1 using an administrator account.

Execute a backup task on the Network Switch.

After the backup task is complete, log into the Network Switch and perform a configuration change.

Re-execute the backup task in CatTools.

Open File Explorer and navigate to “C:\Backups\Switches\Reports\ConfigChanges”.

A list of files will be shown, open the latest one by double clicking it.

Review the Report and verify that the report identifies what was changed on the Network Switch.

| Description | Comments & Observations |
| --- | --- |
| Use the reports function to verify any network switch changes that can be documented. |  |
| Expected Result to pass: |  |
| The CatTools application will identify the changes made to the device under test. |  |

Verify Network Switches have a customer approved banner during sign in (Optional)

This task is to verify the Network Switches have a customer approved banner during sign in:

Log into the DR1 using an administrator.

Open File Explorer and navigate to “C:\Backup\Switches\Config”. Open the config of the Network Switches and review the file for the customer approved banner.

Verify the Network Switch has the customer approved banner.

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switch displays the customer approved banner during sign in. |  |
| Expected Result to pass: |  |
| Verify the Network Switch displays the customer approved banner. |  |

Verify the Network Switches are synced to NTP source

This task is to verify the Network Switches from each network segment (block 1, block 2, DMZ) sync to the proper NTP source:

Log into the DR1 using an administrator account and launch the CatTools shortcut on the desktop.

On the left panel, under the “Devices” tab, a list of devices will be listed. Double click on the Network Switch device listed.

Login to the Network Switch and verify the switch has the correct NTP Source at the end of the config.

Verify NTP status of the switch “show ntp status”

Verify NTP associations of the switch “show ntp associations”

Verify Switch time “show Clock”

| Description | Comments & Observations |
| --- | --- |
| Verify the Network Switches are synced to the correct NTP Source at the end of the config.sh | NTP Source: _____________________________ |
| Expected Result to pass: |  |
| Verify the Network Switches have the correct NTP source added successfully at the end of the config. |  |

Disable any Unused Ports (Optional) based on the project scope this may be executed at the time of COD.

If requested at the time of CWT, this task is to verify the Network Switches have the appropriate unused ports disabled.

Log into the DR1 using an administrator.

Open File Explorer and navigate to “C:\Backup\Switches\Config”. Open the config of the Network Switches and review the file looking for the unused ports with the shutdown command applied.

Sign into the Network Switch and verify the applicable ports have had the shutdown command applied to the unused ports.

| Description | Comments & Observations |
| --- | --- |
| Verify Network Switches have any unused ports shutdown. |  |
| Expected Result to pass: |  |
| Verify the Network Switches have successfully shutdown the appropriate unused ports. |  |

NTP

Verify NTP Synchronization

This task is to verify if the domain controllersfrom each network segment (block 1, block 2, DMZ) are synced to the proper NTP Server:

Log into the DC using an administrator account.

Open the Admin Command Prompt and type: “w32tm /query /peers” <Enter>

Verify the system is pointing to the correct NTP IP Address.

| Description | Comments & Observations |
| --- | --- |
| Verify DC1/ DC2 is synced to the proper time source. | NTP Source: ______________ |
| Expected Result to pass: |  |
| Verify the Domain Server is pointing at the correct time source. |  |

Verify Servers Sync to NTP Server (HMI’s Excluded)

This task is to verify if the OTArmor Servers from each network segment (block 1, block 2, DMZ) are synced to the Active Domain Controller for the respective network segment:

Log into each Servers using an administrator account.

Open the Admin Command Prompt and type: “w32tm /query /peers” <Enter>.

Verify the system is pointing to the Active Domain Controller IP Address.

| Description | Comments & Observations |
| --- | --- |
| Verifying all Servers are synced to DC1. |  |
| Expected Result to pass: |  |
| Verify the servers are pointing at the correct Active Domain Controllers. |  |

Account Management

Default/Domain Accounts

This task is to verify only the applicable Users are enabled in the Domain for the respective network segment (block 1, block 2, DMZ) in HMI/Servers/NTP/Default Switches:

For each network segment (block 1, block 2, DMZ), log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers”Select “Tools->Active Directory Users and Computers” and review the Windows user accounts present.

Verify only necessary accounts are present and enabled. Default windows accounts not required are disabled or removed.

To check the local Users on the HMIs/Servers:

Log into the HMI and open “Control Panel -> All Control Panel Items-> Administrative Tools -> Computer Management -> Local Users and Groups -> Users”.

Review the windows user accounts present.

Verify only necessary accounts are present and enabled. Default windows accounts not required are disabled or removed.

| Description | Comments & Observations |
| --- | --- |
| Verify Windows default accounts have been deleted, disabled or renamed on the HMIs, Default Switches, NTP Server and Servers. |  |
| Expected Result to pass: |  |
| All the Accounts that are not going to be used should be disabled. In the comments list all the accounts disabled. |  |

Verify Operator Account

This task is to verify the Operator account settings to comply with Customer needs for the controls network segments (block 1, block 2):

Log into the HMI using the GEOper account.

Verify the privileges that the account has:

Verify there is no access to the Command Prompt, no ability to Navigate to the hard drives, and cannot Open the Control Panel.

If needed, make changes on the account and describe them under “Comments & Observations”.

| Description | Comments & Observations |
| --- | --- |
| Verify ‘Operator’ account has least amount of user privileges. Accounts should not have any Admin rights. |  |
| Expected Result to pass: |  |
| Verify Operator Account does not have an Administrator Account. |  |

Verify Engineer/Maintenance Account

This task is to verify the Engineer/Maintenance account settings comply with Customer needs for the controls network segments (block 1, block 2):

Log into the HMI using the GEMaint account.

Verify the privileges of the account by:

Opening the Command Prompt, navigate to the C: drive, Verify the. TCW is not in “Read-Only” mode, Open Control Panel and verify user has access and can make changes.

If needed, make changes on the account and describe them under “Comments & Observations”.

| Description | Comments & Observations |
| --- | --- |
| Verify ‘Engineer/Maintenance’ account has the right user privileges. Account should have Maintenance rights. |  |
| Expected Result to pass: |  |
| Verify Engineer/Maintenance Account has Command Prompt, Control Panel Access, can make changes in the E: Drive and. TCW. |  |

Verify Shared Accounts

This task is to verify all shared accounts on the controls network segments (block 1, block 2):

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Select “Tools->Active Directory Users and Computers” and identify which users are shared Accounts. (A shared Account is when more than one person can access and login with an account).

- Standard default shared accounts are mentioned below

- GEAdmin

- GEMaint

- GEOper

| Description | Comments & Observations |
| --- | --- |
| Identify any shared accounts and if they are needed. |  |
| Expected Result to pass: |  |
| List under comments all the shared Accounts found. |  |

Service Accounts

This task is to verify all service accounts for each network segment (block 1, block 2, DMZ):

Log into any of the DC using admin account and launch “Server Manager”.

Select “Tools -> Group Policy Management”.

Under “Domain Name (HMI.local)-> GEV Controls->Domain Controllers ->GEV DCx Hardening Policy”. Select “Settings” tab and review the service accounts listed under “Deny Log on Locally”. Verify the User Group “Deny Log Locally” is listed.

Under “Domain Name (HMI.local)-> GEV Controls -> HMI->Windows 10 HMI -> GEV Win10 Hardening Policy”. Select “Settings” tab and review the service accounts listed under “Deny Log on Locally”. Verify the User Group “Deny Log Locally” is listed.

Under “Domain Name (HMI.local)-> GEV Controls -> OTArmor Servers-> GEV Server OS Hardening Policy”. Select “Settings” tab and review the service accounts listed under “Deny Log on Locally”. Verify the User Group “Deny Log Locally” is listed.

Select “Tools -> Active Directory Users and Computers”. Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Select “Tools->Active Directory Users and Computers”. Double click “Deny Log Locally” User group and choose “Member of” tab. Verify the list of users.

| Description | Comments & Observations |
| --- | --- |
| Identify any accounts associated with automated functions. |  |
| Expected Result to pass: |  |
| List under comments all the service Accounts found. |  |

Verify Service Account Restrictions

This task is to verify all service accounts cannot login into windows locally for each network segment (block 1, block 2, DMZ):

Log into the HMI trying to use any of the service accounts.

A message stating the Account cannot be log in should appear.

| Description | Comments & Observations |
| --- | --- |
| Verify these accounts cannot be used to log into Windows: • “Deny Log on Locally” is set |  |
| Expected Result to pass: |  |
| Login should fail with a message stating the account is a service Account. Record the name of the account(s) tested. |  |

Verify Service Account Password Policy

This task is to verify all service accounts for each network segment (block 1, block 2, DMZ) have their password set to never expire:

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Select “Tools->Active Directory Users and Computers” and identify a service Account.

Double click it and under” Account” tab (in the Account Options), make sure “Password Never Expires” is checked.

| Description | Comments & Observations |
| --- | --- |
| Verify these accounts have their passwords set to never expire. |  |
| Expected Result to pass: |  |
| Each Account should show the ‘Password never expires’ checked. Record the name of the account(s) tested. |  |

Domain Password Policy Settings

This task is to verify the Domain Password Policies are setup correctly for each network segment (block 1, block 2, DMZ):

    - Log into any of the Domain controllers using admin accounts.

    - Open “Server Manager”.

    - Select “Tools -> Group Policy Management”.

    - Expand “Forest. Domain Name (HMI.local) -> Domains -> Domain Name (HMI.local)-> GEV Site Customization Policy

- ” And click “Edit”. Expand the following path “Computer configuration-> Policies-> Windows Settings->Security Settings -> Account Policies -> Password Policy”.

Verify each of the items listed below and make sure the settings are correct on the policies mentioned above:

- Enforce Password History = 24 Passwords

- Maximum Password Age = 90 Days

- Minimum Password Age = 1 Day

- Minimum Password Length = 8 Characters

- Password must meet complexity requirements = Enabled

| Description | Comments & Observations |
| --- | --- |
| Verify OTArmor Domain Policy password policy is set to: Enforce Password History = 24 Passwords Maximum Password Age = 90 Days Minimum Password Age = 1 Day Minimum Password Length = 8 Characters Password must meet complexity requirements = Enabled |  |
| Expected Result to pass: |  |
| Make sure each setting is correctly set as per list above. |  |

Verify Password Policy on Domain Accounts

This task is to verify the Password Policy is enforcing the passwords in new domain accounts for each network segment (block 1, block 2, DMZ):

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Right click on “GEV Users and Computers”, then choose “New -> User”.

Select a name for the username and click “Next”. Enter a simple password to test the enforcement and click “Next” and then “Finish”. An error pops up will appear stating the password does not meet the Password Policy requirement.

Attempt to set the user password again, this time apply a complex password meeting the settings on previous step.

Verify the user password is accepted.

Delete the account after the password is verified.

| Description | Comments & Observations |
| --- | --- |
| Create a dummy domain account and test password policy is being enforced. Delete account when finished. |  |
| Expected Result to pass: |  |
| Verify the account can be created when the password meets the password enforcement established on the Domain. |  |

Verify Password Policy on Local Accounts

This task is to verify Password Policy enforcing the password in new local accounts for each network segment (block 1, block 2, DMZ):

Log into an HMI using admin account.

Open “Control Panel -> All Control Panel Items-> Administrative Tools -> Computer Management -> Local Users and Groups -> Users”. Right click on “Users”, then choose “New User”.

Select a name for the username and click “Next”. Enter a simple password to test the enforcement and click “Next” and then “Finish”. An error pops up will appear stating the password does not meet the Password Policy requirement.

Attempt to set the user password again, this time apply a complex password meeting the Password Policy settings above.

Verify the user password is accepted.

Delete the account after the password is verified.

| Description | Comments & Observations |
| --- | --- |
| Create a dummy HMI local account and test password policy is being enforced. Delete account when finished. |  |
| Expected Result to pass: |  |
| Verify the account can be created when the password meets the password enforcement criteria established. |  |

Account Lockout

This task is to verify any user can be locked out after 10 failure login attempts on each network segment (block 1, block 2, DMZ):

Choose an account other than the Administrator account and attempt to login to a server with a wrong password. Repeat this step 10 times.

After the 10th failure, attempt to login with the correct password. A message should appear stating the Account has been locked due to many unsuccessful attempts.

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers” Look for the User used on first step.

Once you find the User, right click on it and choose “Properties”. Under the account tab, a message will appear stating the account is locked.

Log out of the Domain Controller.

| Description | Comments & Observations |
| --- | --- |
| Verify if the incorrect password is entered more than 10 times a user account is locked out. | Account Tested: ____________ |
| Expected Result to pass: |  |
| Verify the account is locked out after 10 unsuccessful attempts. |  |

Verify Account Reset after Lockout

This task is to verify any user locked out from each network segment (block 1, block 2, DMZ) can be reset and log in again:

Identify the account locked out in the previous test case.

Log into any of the DC using an administrator account. Open Server Manager, on the top menu chose “Tools-> Active Directory Users and Computers”.

A new window will appear (Active Directory Users and computers), expand “Domain Name (HMI.local)->GEV Controls->GEV Users and Computers”. Look for the User you use on first step.

Once you find the User, right click on it and choose “Properties”. Under the account tab, a message will appear stating the account is locked

Check the “Unlock Account” and click OK.

Try to login with this user with the correct password. This time you should be able to login.

| Description | Comments & Observations |
| --- | --- |
| Verify account can be reset after lockout. | Account Tested: ___________ |
| Expected Result to pass: |  |
| Verify the account is reset and can login again. |  |

Windows Patching

Patch Scan and Deployment

This task is to verify the latest PVP disk has been deployed in PM1:

If you have application control, make sure to change Policy to Patching or Update mode in Trellix EPO for PM1. If not, directly proceed with the following steps.

Obtain the updated PVP patch disk or associated .iso file.

Mount the patch disk and execute the update batch file.

Verify the process completes successfully.

| Description | Comments & Observations |
| --- | --- |
| Verify latest GE approved patches are deployed to the Ivanti Console. Update discs will always be one month behind. | Version Used: ____________ |
| Expected Result to pass: |  |
| Verify the PVP disk run successfully. |  |

Verify Device Detection for Patching

This task is to verify all the devices that are detected by Ivanti in PM1 Server:

Log into the PM1 server using an administrator account and launch the Ivanti shortcut on the desktop.

Perform a patch scan of the Domain using the pre-defined GE patch list.

Verify Ivanti lists all the HMIs, Servers (Virtual Machines) from all network segments (block 1, block 2, DMZ) in the system.

Machine Groups as follows per domain:

- 10.2.4.1 Servers Group:

- OTCA1

- OTDC1

- OTDR1

- OTPM1

- OTSP1

- 10.2.4.2 Early Adopters:

- OTDC2

- 10.2.4.3 Workstationss:

- All other physical and virtual machines

| Description | Comments & Observations |
| --- | --- |
| Verify all HMIs, servers: virtual machines are reporting in the Ivanti console. |  |
| Expected Result to pass: |  |
| After the scan, verify all the devices are listed. |  |

Verify Patch Deployment

This task is to verify all the devices that are detected by Ivanti in PM1 Server, and we can deploy patches into them:

Log into the PM1 server using an administrator account and launch the Ivanti shortcut on the desktop.

Perform a patch scan of the Domain using the pre-defined GE patch list.

Verify it lists all the HMIs, Servers (Virtual Machines) in the system.

Deploy all missing patches in a chosen HMI/Server. Verify that a “Patching in progress” message is displayed on the target machines.

If necessary, reboot the systems being patched when the patches complete deploying.

Perform a patch scan of the HMI/Server chosen using the pre-defined GE patch list, verify that the patches deployed no longer show as required.

If any new patches show as required, deploy the patches to the systems. If necessary, reboot the systems being patched when the patches complete deploying.

Repeat this process and verify the systems can be patched with no missing patches present.

| Description | Comments & Observations |
| --- | --- |
| Scan the network and deploy any missing patches or service packs. Reboot HMIs/Servers as necessary. |  |
| Expected Result to pass: |  |
| Verify patches can be deployed in devices listed on Ivanti console. |  |

HMI Backup & Restore

Perform Backups

This task is to verify Acronis has the backup plans set for all HMIs\Servers for each network segment (block 1, block 2, DMZ):

Log into the DR1 system using an administrator account and connect to Acronis Management Server.

Select Backup Plans.

Make sure we have defined a Backup Plan for OTArmor Servers.

Make sure we have defined a Backup Plan for HMIs

On each backup plan verify the configuration of it. Right click on the backup plan and choose “Edit”.

The backup plan configuration determines the rate of backups, as well as how long they are kept. There are three types of backups:

- 12.1.5.1 Full – A complete backup of the machine.

- 12.1.5.2 Differential – A backup of changes that have occurred since the last Full backup.

- 12.1.5.3 Incremental – A backup of changes that have occurred since the last Differential backup.

There is a plan present for every asset.

All plans present a green status.

What to back up: Entire Machine

Where to back up: //NAS/Backup

How long to keep:

Full: 6 Months

Differential: 4 Weeks

Incremental: 7 Days

| Description | Comments & Observations |
| --- | --- |
| Verify all HMIs/Servers are in the backup plan in the Acronis Management Console. |  |
| Expected Result to pass: |  |
| Verify back up plans were created that includes all the Windows devices. |  |

Verify Restore Activities for Files/Folders.

This task is to verify Acronis can restore Files /Folders.

Log into the DR1 system using an administrator account and connect to the Acronis Management Server.

Select DR1 on the All-Devices page.

Choose the Recovery > Recover… > Files/Folders option on the right:

Select C:\bginfo\ and select Download from the right.

Once the download is completed, verify that the folder can be opened, and the image inside can be viewed.

| Description | Comments & Observations |
| --- | --- |
| Verify an HMI files/Folders can be restored in case of a disaster recovery by using the Acronis backup | HMI Restored: ____________ |
| Expected Result to pass: |  |
| Verify Acronis Restore executes successfully. Take note of the Files/Folders restored under Comments & Observations. |  |

Verify Restore Activities for Thick HMIs.

This task is to verify Acronis can restore an HMI from the controls network segments (block 1, block 2):

Log into the DR1 system using an administrator account and connect to the Acronis Management Server.

Create recovery media in the Acronis console in the CD/USB format.

Select an HMI to recover, record the machine name below.

Log into the machine to be recovered. Execute an incremental backup of the machine.

When the backup is complete, create a file on the computer desktop.

Reboot the system to the physical CD/USB recovery media, restore the most current backup of the virtual system.

When the recovery is complete, log into the system and verify the file doesn’t exist on the desktop.

| Description | Comments & Observations |
| --- | --- |
| Verify an HMI can be restored in case of a disaster recovery by using the Acronis Boot Disc. | HMI Restored: ____________ |
| Expected Result to pass: |  |
| Verify Acronis Restore executes successfully. Take note of the HMI restored under Comments & Observations. |  |

Verify System After Restore.

This task is to verify functionality after the restore from the previous step:

Log into the HMI/Server restored using an administrator account.

Verify the name of the HMI(s) and IP Address.

Log into PM1 using an administrator account, verify Ivanti can scan the HMI/Server.

Log into LM1 using an administrator account, verify Splunk can receive logs from the HMI/Server.

Log into DR1 using an administrator account, verify Acronis can scan the HMI/Server.

| Description | Comments & Observations |
| --- | --- |
| Verify the following after the restore is complete: • Machine name and IP address are correct • HMI is reporting in McAfee/Trend Micro/Splunk, Acronis and Ivanti. |  |
| Expected Result to pass: |  |
| Verify name and IP Address are correct in the HMI restored. Verify HMI is recognized by our different Server applications. |  |

NETWORK SECURITY MONITORING

Monitoring Port

Physically verify Nozomi device connections.

Verify if the ports are connected to a span port in the switches.

Connect to the switches for the respective network segment (block 1, block 2) through DR1/CatTools and verify if that port is a SPAN Port.

| Description | Comments & Observations |
| --- | --- |
| Ensure that Nozomi Guardian ports are connected to the span port of network switch. |  |
| Expected Result to pass: |  |
| Verify SPAN port is configured in switch through CatTools and is there’s a connection to the Nozomi Guardian as per Topology. |  |

Nozomi Dashboard

Open a web browser and connect to Nozomi for the respective network segment (block 1, block 2).

Verify if dashboard is populating data.

| Description | Comments & Observations |
| --- | --- |
| Verify if data is populated in the Dashboard (Assets, Nodes, Sessions). |  |
| Expected Result to pass: |  |
| Data is shown in Nozomi Dashboard. |  |

Network Traffic Validation

This task is to Verify the appliance is observing Network Traffic for the respective network segment (block 1, block 2)

On the web GUI, go to Administration > Network Interfaces. Make sure that the Throughput graph is being updated live with network data from all the applicable monitoring interfaces.

On the web GUI, go to Environment > Network view > Traffic tab. Make sure that the graphs are getting populated with live data information.

| Description | Comments & Observations |
| --- | --- |
| Verify if the network traffic in network view Traffic tab populated live data information |  |
| Expected Result to pass: |  |
| Can see live data information in traffic tab. |  |

Passive Monitoring and Network modeling and visualization Operation

This task is to verify that Nozomi IDS appliances for the respective blocks (block 1, block 2) show assets in the network with correct information.

On the Network View > Nodes tab, verify that this data is getting populated:

- Address

- Role

- Type

- MAC address

- Protocols

- On the Asset view, verify that this data is getting populated:

- Name

- Address

- Role

- Type

- OS/Firmware

On the Network View > Links tab, verify this data is getting populated:

- From

- To

- Protocol

- First Activity

- Last Activity

- Throughput

On the Network View > Session’s tab, verify that this data is getting populated:

- Status (review that you have sessions with Status SYN, ACTIVE and CLOSED)

- From

- To

- Protocol

On the Network View > Graph tab, check that the network graph is being displayed. Apply various filters

| Description | Comments & Observations |
| --- | --- |
| Verify that Nozomi IDS appliance shows assets in the network with correct information |  |
| Expected Result to pass: |  |
| Can see live data populated in network view |  |

Learning Mode Configuration

This task is to verify Nozomi IDS appliance for the respective block (block 1, block 2) is configured in Learning mode.

Login to Nozomi web interface

Select Administration-> Security Control Panel->

Click on “1-Learning” on left-hand pane

Under “Phase Switching”, select “Two Phase” and then “Learning”

Click “Save”

| Description | Comments & Observations |
| --- | --- |
| Verify that Nozomi IDS appliance is configured in Learning mode |  |
| Expected Result to pass: |  |
| Can see Nozomi IDS appliance is configured learning mode |  |

Malicious Signature detection

Open a web browser and connect to Nozomi.

Copy Antivirus EICAR file and proceed to copy through the network to another asset for each block being monitored (block 1, block 2).

Very Nozomi triggers an alert.

| Description | Comments & Observations |
| --- | --- |
| Verify the popup warning is presented after copying the Test Virus file to a remote system. |  |
| Expected Result to pass: |  |
| Alert triggered after copy of virus file via network. |  |

TRELLIX

Trellix Agent

This task is to verify all the devices on each network segment (block 1, block 2, DMZ) that are detected by Trellix ePO in OTSP1:

Log into the OTSP1 using an administrator account and launch the Trellix ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Confirm that the machines with the System Tree are organized into the correct groups and appear as ePO managed endpoints

HMIs

OTArmor Servers

| Description | Comments & Observations |
| --- | --- |
| Verify all HMIs and Virtual machines are reporting in the Trellix Management Console. |  |
| Expected Result to pass: |  |
| Verify all the devices are listed in the Trellix ePO management console. |  |

Verify ePO Virus Definitions

This task is to update the virus definitions and verify the version of AV in Trellix ePO in SP1

Log into the SP1 using an administrator account and launch the Trellix ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “Menu -> Software-> Master Repository”. Click “Check In Package”.

Select Product or Update (.zip) as the package type and browse to select the package with the new definitions and select “Open”

Click Next to view the package check-in summary information.

Select “Branch -> Current”.

Click “Save” to begin the check-in. Wait until the Check-in is complete and click Close.

Ensure the new virus definition package is in the repository:

Click “Menu->Software->Master Repository”.

Search the DAT in the name column.

Verify that the DAT version displayed is the same as the version you checked in.

| Description | Comments & Observations |
| --- | --- |
| Verify the latest AV signatures are installed into the management console. | Version Used: ____________ |
| Expected Result to pass: |  |
| Verify the version of AV in Trellix console. |  |

Verify ePO Software Deployment

This task is to verify the versions of AV on each HMI/Server for each network segment (block 1, block 2, DMZ) match the Trellix ePO in SP1:

Log into the SP1 using an administrator account and launch the Trellix ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “System Tree View -> Systems tab-> Preset: This Group and all Subgroups”. Click on the name of the HMI/Server to verify and choose the “Products” tab.

A list of the products and the version of each will be listed.

Now login into the HMI/Server. In the bottom right in the task bar, a Trellix icon should be present.

Right click on the Trellix icon and click “About”. A list of all the products installed will appear. Verify the versions match the ePO console Products tab for Trellix Data Exchange Layer, Trellix Application Control, Trellix Agent and Trellix DLP Endpoint.

Right click on the Trellix icon and click “Trellix Endpoint Security -> About”. A list of all the products installed will appear. Verify the versions match the ePO console -> Products tab for Endpoint Security Platform and Threat Prevention.

| Description | Comments & Observations |
| --- | --- |
| Verify all machines are up to date with management console. Check locally each HMI has the same definition level as management console. |  |
| Expected Result to pass: |  |
| Verify the version of AV matches from HMI/Servers to the ePO console. |  |

Verify Antivirus Software Operation

This task is to verify viruses that are being detected by the HMI/Server of each network segment (block 1, block 2, DMZ) and Trellix ePO in SP1 and they can be removed from the system:

Log into an HMI/Server using an administrator account. Open file explorer and type this path: \\ca1\Admin_Procedures\OTArmor. Locate the “Test-Antivirus” and copy it into the desktop of the HMI/Server to be tested.

Right click on “Test-Antivirus” and choose “Run with Powershell”. Once the Powershell was run a pop up should appear from Trellix stating a virus was detected.

- Note: If the system has Solidcore installed, it will be necessary to add the powershell script to Solidcore rules to be allowed to run in “Enabled” mode.

Log into the SP1 server using an administrator account and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “Tree View -> System tab-> Preset: This Group and all Subgroups”. Click on the name of the HMI/Server to verify and choose the “Threat Events” tab.

A list of threat will be presented, select the one generated as part of the testing and click on “Actions -> Delete”.

| Description | Comments & Observations |
| --- | --- |
| Apply a test virus to an HMI. Verify is detected on the HMI, in the Trellix Management Console. |  |
| Expected Result to pass: |  |
| Verify the virus is detected by Trellix in the HMI/Server and ePO. |  |

Verify USB Device Restrictions

This task is to verify access to USB devices is restricted for users of each network segment (block 1, block 2, DMZ) without authorization:

Log into an HMI using the “GEMaint” account. Insert an encrypted USB to be tested.

Under this account, a pop up should appear explaining DLP has blocked the device.

Attempt to access files on the device and verify an “Access Denied” message is received when trying to get the USB’s contents.

Log into the SP1 server using an administrator account and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to Menu -> Policy Catalog -> Data Loss Prevention 11.X -> under policy - GEV Block All Devices”. Select “Edit -> GEV Removable Storage Device Rule -> Device Control -> GEV Block Removable Device Rule, choose “Exceptions” tab and choose “Excluded Users”. Verify that the GEMaint account does not have a USB exception.

| Description | Comments & Observations |
| --- | --- |
| Verify USB devices can NOT be accessed when an HMI logs in with a different user account from the exception. |  |
| Expected Result to pass: |  |
| Verify there’s NOT access to USB devices with the incorrect exception User Account. |  |

SolidCore

This task is to verify SolidCore is working properly.

Changing Status

Log into each HMI/Server from ach network segment (block 1, block 2, DMZ) with an administrator account.

Open an administrator command prompt and verify the system is solidified, in enable mode, in lock down mode and is managed by the ePO server

Log into the SP1 with administrator credentials and launch the ePO web management interface shortcut on the desktop.

Log in using the ePO administrator account.

Go to “System Tree”, click on “My Organization” and select all the devices listed and under “Actions” select “Agent”-> “Run Client Task Now”. A new screen will show up, on the left pane select “SolidCore 8.X.X”. At the middle pane select “Begin Update Mode”. At the right pane select “Create new task” and click on “Run Task Now”.

Wait until the task completes.

On HMI/Server, open an administrator command prompt and verify the system is in Update mode.

Repeat steps to change into different modes

Switching between modes

From Observe mode, you can switch to Enabled or Disabled mode.

From Enabled mode, you can switch to Disabled, Update, or Observe mode.

From Update mode, you can switch to Enabled or Disabled mode.

From Disabled mode, you can switch to Enabled, Update, or Observe mode.

| Description | Comments & Observations |
| --- | --- |
| Verify the change on the mode status is working. |  |
| Expected Result to pass: |  |
| Verify change of status executes successfully. |  |

Testing SolidCore Application

Log into the DR1 Server with an administrator account.

Open an administrator command prompt and verify the system is solidified, in enable mode, in lock down mode, and is managed by the ePO server.

Locate the “putty.exe” file and copy the application to a HMI’s desktop.

On the HMI, open an administrator command prompt and verify the HMI is solidified, in enable mode, in lock down mode, and is managed by the ePO server.

Attempt to execute the putty application on the desktop. Verify that the application is blocked by whitelisting.

From the ePO server, place the HMI in update mode.

Verify the HMI is in update mode. Erase and copy Putty again and attempt to run the application on the desktop. Verify the file is permitted to be executed.

From the ePO server, remove the system from update mode to enable mode. Verify the HMI that it is in enable mode.

Attempt to execute the Putty application on the desktop, verify that the application is permitted to execute.

| Description | Comments & Observations |
| --- | --- |
| Verify Putty cannot be run unless in update mode. |  |
| Expected Result to pass: |  |
| Verify running Putty gets denied by solidcore and allows it when in update mode. |  |

SIEM

The following test items are designed to verify functionality and configuration of the Security Incident     and Event Monitoring (SIEM) capabilities provided by the security appliance.

SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards

Demonstrate the following widgets displayed on the GE Default dashboard & are populated with event data:

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

In view “GE Dashboard” consists of below events.

Windows Device Events.

Network Device Events.

VMware Device Events.

Events count by Host

Events

Failed Login by user.

Open the NERC-CIP 002 Dashboard and confirm the widgets are populating with event data

| Description | Comments & Observations |
| --- | --- |
| - Verify GE Default dashboard & are populated with event data: - Windows Device Events - Network Device Events - VMWare Device Events - Event Summary - Event count by Host - Events - Failed Login by User - NERC-CIP 002 Dashboard |  |
| Expected Result to pass: |  |
| Verify all the devices events are populated in GE Default SEM dashboard. |  |

Verify Asset Listing

Verify that all applicable assets are listed in the Trellix SIEM appliance, and are populated within their respective Asset Groups from each network segment (block 1, block 2, DMZ)

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

From the ESM Dashboard menu, Select Asset Manager.

In Asset Manager click on Asset tab you can see the list of Asset Groups as defined below.

VMware

Windows

Network devices

Non-Windows

| Description | Comments & Observations |
| --- | --- |
| Verify all Devices are added in Asset Groups as defined below. - VMware - Windows - Network devices - Non-Windows |  |
| Expected Result to pass: |  |
| Verify all the devices are listed in Asset groups. |  |

Verify Data Sources in Local Receiver – ELM.

Verify that all applicable data sources are listed in the Trellix SIEM appliance, and the correct properties are assigned to each one.

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

From the ESM Dashboard menu, Select ELM Search.

From the Configuration tab, select Local Receiver-ELM and click Properties ()

In the receiver /ELM Properties – Local Receiver – ELM windows, select Data sources and verify all Devices are added in Data sources list from each network segment (block 1, block 2, DMZ).

| Description | Comments & Observations |
| --- | --- |
| Verify that all devices’ data sources are listed in the Trellix SIEM appliance, and the correct properties are assigned to each one. |  |
| Expected Result to pass: |  |
| Verify all the devices are listed in the Data sources list |  |

Verify Event Logging

Verify that an event is displayed in the Windows Login Events widget of the GE Default Dashboard after a successful or invalid login attempt.

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

In view “GE Dashboard” we can see windows login events.

| Description | Comments & Observations |
| --- | --- |
| Verify that an event is displayed in the Windows Login Events widget of the GE Default Dashboard after a successful or invalid login attempt. |  |
| Expected Result to pass: |  |
| Verify all windows login events are displayed in Windows login events Widget. |  |

SIEM Report Generation

Verify that a selected report can be generated and contains relevant event data

Login to the SIEM Server with admin credentials.

Open “Trellix Enterprise security manager Administrator console” shortcut desktop.

From the ESM dashboard menu, select System properties

In the system properties tree, select Reports and click on add and generate report.

Click on files, and in the files, list select file and click on download the report.

| Description | Comments & Observations |
| --- | --- |
| Verify that a selected report can be generated and contains relevant event data. . |  |
| Expected Result to pass: |  |
| Verify that a selected report can be generated and downloaded successfully. |  |

Controller Hardening

This test case is applicable to both Block 1 and Block 2 using the block specific domain components, not the OTArmor domain components

Secure Mode

This task is to verify the Mark VIe controllers can be put into Secure Mode.

In Toolbox, verify the Mark VIe controllers can be put into Secure Mode.

In CA1, verify the CA1 server is issuing a certificate for the controllers.

Remove controller from secure mode.

| Description | Comments & Observations |
| --- | --- |
| Verify the Mark VIe Controller can be put into Secure Mode. Ensure CA1 is issuing certificates for the controller. |  |
| Expected Result to pass: |  |
| Verify that the Mark VIe Controller can be put into Secure Mode, CA1 is issuing certificates for the controller. |  |

- HIGH AVAILABILITY FAIL-OVER

This test case is applicable to Block 1, Block 2, and the Cybersecurity DMZ

    - Verify OTVH1, OTVH2 and OTVH3 are running. All VM’s on each hypervisor must be on and operating normally (Skyline Health good and make sure unhealth items in VSAN health).

    - Remove the power cables from one of the Hypervisors (OTVH1 or OTVH2 or OTVH3).

    - Login into vSphere with admin credentials. Verify all the Virtual Machines associated with the Hypervisor chosen are migrating to their corresponding backup Hypervisors.

- Note. This step takes time, the change is not instant.

    - Reconnect the power cables to the Hypervisor chosen earlier

    - Manually migrate all the Virtual machines that belong to the chosen Hypervisor back:

      - Right click on the VM, select “Edit Settings” and Uncheck the CD Drive. Click “Save”.

      - Right click on the VM, select “Migrate” ->” Computer Resources” ->” Next”->” Finish”.

    - Verify the migration of the VM’s involved have been successful.

| Description | Comments & Observations |
| --- | --- |
| Verify the Virtual Machines associated with VHx move to its corresponding backup server. Return the power to VHx and manually migrate the VM’s to their original Virtual Host. Verify the migration is executed successfully. |  |
| Expected Result to pass: |  |
| Verify HA fail-over is performed successfully. All VMs migrate to the rest of the Hypervisors. Verify after re-establishing, that all VM’s can be migrated to their original Hypervisor. |  |

AGREED RESIDUAL ACTIONS

Description:

Identify residual actions related to the above test cases, questions, agreements, or any other issues to be addressed after the CWT but before installation starts. Include who will be doing the work and the estimated completion date.  Additional residual action lists may be attached at the end of this document as needed.

| Item # | Description of Change or Action | Action Item Owner | Estimated Completion Date |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |
| 9 |  |  |  |
| 10 |  |  |  |
| 11 |  |  |  |

CUSTOMER WITNESS TEST SIGNATURE SHEET

The undersigned agree that the Customer Witness Test was completed on the date indicated.

GEV	CUSTOMER

Approval	Attendance

___________________________________	___________________________________

(signature)	(signature)

______________	______________

(date)	(date)

CUSTOMER WITNESS TEST

The following approvals constitute the satisfactory completion of the Customer Witness Test (CWT).

The CWT was conducted on a structured basis as outlined in the previous pages.

The above signatures constitute an agreement on the outstanding residual actions and a commitment by GEV to resolve and/or complete any outstanding action items.  Outstanding items are identified on the Agreed Residual Action Items list or as an attachment to this document.

Customer’s signature authorizes the billing associated with the Customer Witness Test completion.

In an effort for continuous improvement, GE Vernova requests all customers fill out the survey at this link at the conclusion of the CWT.