## Slide 1: Gas Turbine Model Based Controls
Prabhanjana Kalya

## Slide 2: Objectives
  Where MBC fits in GT controls
  Fundamentals of MBC
  Advantages of MBC
  Cycle versus Combustion Controls
  Concept of Load Path and its advancements
  Design of some of components of MBC software suite
The objective of this class is to explain

## Slide 3
Critical Controls Questions:
  What are my operational missions?
  What are my operating limits?
  What are my effectors / sensors?
  What are my control objectives?
  What are my noise/disturbance parameters/events?
GT Controls Design:
  MBC Overview
  MBC control design examples
Introduction

## Slide 4
What are my operational missions?
Normal Operation
Off
Turning Gear
Crank
Purge
Decel. to Ignition
Fire
Accelerate
Full Speed No Load
Synchronize
Spinning Reserve
Emissions Compliant Turndown
Preselect Load
Base Load
Peak Load
Power Augmentation
Reserve Margin
Unload
Deceleration
Coast Down
Cooldown
Protective Missions
Trip
Shutdown
Runback (normal, fast)
Load Rejection
Step to Spinning Reserve
Fuel Transfers
Gas-to-liquid
Liquid-to-gas
DLN Mode Transfers
Many
Gas Turbine Missions

## Slide 5
What are my operating limits?
(9FB Example)
Gas Turbine Limits

## Slide 6
What are my operating limits?
(9FB Example)
Gas Turbine Limits

## Slide 7: MBC in GT Controls
Prestart
Purge
Fire & Warmup
Acceleration
Sync & Temp Match
Loading
%TNH
%Load
MBC
ENABLED

## Slide 8: Commonly used GT control loop structure
Co
Outer Loop
Ci
Gi
Go
Inner Loop
+
-
+
-
C
G
+
-
C
G
+
-
FF
Ref
e
Controller
output
Plant
output
Sensor outputs
OR
Model outputs
Ex. : Isotherm TTXM = 1200
Targets/ Boundary
+
Ref
Ref
Controller
output
Plant
output
Servo
O/P
IGV = ## Deg
TTXM
Targets/ Boundary
Sensor outputs
OR
Model outputs
Targets/ Boundary
FF output
+
Controller output

## Slide 9
What are my effectors?
Legend:
IGV
TTXM
– critical
effectors
– critical
sensors
(F)
(Units)
IGV
PM1
PM4
D5
IBH
TTXM
CTD
CPD
CTIM
TNH
SRV
FPG2
DWATT
~
Other Critical Control Parameters:
TFIRE- Firing temperature
CRT – Combustion reference temperature
TNHCOR – inlet temp-corrected speed
CPR – compressor pressure ratio
AFPCS
AFPAP
ATID
(MW)
(inHg)
(F)
(psig)
(F)
(%)
(F)
(inH2O)
(psig)
(F)
C
Comb
T
What is FSR?
FSR stands for Fuel Stroke Reference. FSR is the key fuel control output, designed to be proportional to the fuel heat consumption (BTU/sec). FSR can be thought of as though there it were the position of a single “virtual” gas control valve for the turbine.
What are fuel splits?
A “split” is the proportion of fuel that is delivered to a particular combustion gas passage. In any given DLN system design with N valves, there are N-1 split effectors (since the sum of the fuel is prescribed by FSR, you lose one degree of freedom in splits).
Gas Turbine Effectors / Sensors
What is IGV?
What is IBH?
IGV stands for Inlet Guide Vanes. IGV (csrgv signal name) refers to the vanes at the compressor inlet that affect air flow. Opening the IGV increases air flow through the compressor and hence the gas turbine.
IBH stands for Inlet Bleed Heat. IBH refers to recycling compressor outlet flow back to the compressor inlet. IBH acts to increase air flow through the compressor while decreasing air flow through the gas turbine. The primary use is Compressor surge and icing protection.

## Slide 10
What are my Sensors?
Legend:
IGV
TTXM
– critical
effectors
– critical
sensors
(F)
(Units)
IGV
PM1
PM4
D5
IBH
TTXM
CTD
CPD
CTIM
TNH
SRV
FPG2
DWATT
~
AFPCS
AFPAP
ATID
(MW)
(inHg)
(F)
(psig)
(F)
(%)
(F)
(inH2O)
(psig)
(F)
C
Comb
T
Sensor Signals:
ATID – Ambient Temperature
AFPAP – Ambient Pressure
AFPCS – Inlet Pressure Drop
CTIM – Compressor Inlet Temperature
DWATT – Generator Output
FPG2 – P2 Fuel Pressure
TNH – Shaft Speed as % of Design Point
CPD – Compressor Discharge Pressure
CTD – Compressor Discharge Temperature
TTXM – Exhaust Gas Temperature
Gas Turbine Effectors / Sensors
Other Critical Control Parameters:
TFIRE- Firing temperature
CRT – Combustion reference temperature
TNHCOR – inlet temp-corrected speed
CPR – compressor pressure ratio

## Slide 11: Quiz - 1
Considering normal operation, which is the first effector(after firing) to use ARES for control ?
FSR
FUEL SPLITS
IGV
IBH
ANSWER:
FUEL SPILITS
5 seconds after ARES is enabled Fuel splits are scheduled as a function of CRT (T3.9)

## Slide 12: Nominal Operation Effector – Loop Sequence Cycle Control
Start to FSNL – Start UP Control (SUC)
FSR – Firing->Acceleration/Min->FSRN
IGV – Min
IBH – Min
SPLITS – Per mode sequence
Sync– Base load (CMBC)
FSR – FSRN -> FSRT
IGV – Min -> ISO -> Tfire TG -> Max
IBH – Min ->Max Flow ->CRT ->Min
SPLITS – Per mode sequence ( function of CRT)
No ARES outputs are used
ARES outputs used
CRT, TFIRE, BFM,CM/U…

## Slide 13: Quiz - 2
What does ARES stand for ?
Adaptive Real-time Engine Simulation
Accurate Real-time Estimated Solution
Adaptive Real-time Engine Solution
Adjusted Robust Engine Simulation
ANSWER:
Adaptive Real-time Engine Simulation

## Slide 14: Model-Reference Adaptive Control
Boundary Scheduling Logic
+
_
Model-Based
Control Structure
(Loop Selection Logic)
Boundary/ Targets
Effectors
Errors
Commands
ARES - Parameter
Estimation
Engine Model
Gas Turbine
TF Tuning
Estimated Boundary Levels
Surrogates
Combustion Dynamics Measurement
Boundary Transfer Functions
* Emissions
Measurement
* Closed-Loop Emissions Sensor Part of Development Test Engine(s) – Potentially AO

## Slide 15
What are my control objectives?
What are my noise/disturbance parameters/events?
Again, different per operating mode
Focusing on Gas Fuel, Pre-selected Load operation:
Grid frequency upsets
Fuel pressure, temperature, composition upsets
Swings in compressor inlet conditions (ambient, fogging, chillers, steam heating)
Sensor / effector faults
others…
Objectives change per operating mode
Focusing on Gas Fuel, Pre-selected Load operation:
Deliver requested power
Contribute to grid frequency regulation
Minimize heat rate
Allow Flexibility
Utilize combustion operability
  Minimize dynamics
  Minimize emissions
  Maximize efficiency
  Of course don’t blow out
Standard Droop Speed/Load Control shown:
Gas Turbine Control Objectives

## Slide 16: Model-Based Control v/s CPC
IGV
Fuel Splits
+
_
+
_
+
_
+
_
+
_
+
_
+
_
+
_
+
_
Loop-In-Control
Loop-In-Control
Loop-In-Control
W_fuel
ARES - Parameter
Estimation
Engine Model
Physics-Based Boundary Models
Direct Boundary Protection (In The Boundaries Physical Space)
Accommodation Of Machine Deterioration (Adaptive Model Ensures Accurate Surrogates)
Implicitly De-Coupled Effectors (Automatic Performance Optimization)
Robust / Flexible / Expandable (Additional Boundaries / Loops)
Proven GT Control Technology
Limit Scheduling
Surrogates
Iso-Therm
MINIMUM
Tx_req
Tx
P+I
+
-
W_fuel
/ IGV
TTRF ~ Tx
Splits
TTRF
Fuel
Splits
Approximate Boundary Protection (Accommodate Worst-Case Condition)
No Explicit Accommodation Of Machine Deterioration (New & Clean / Mean Machine Assumption)
Coupled Effectors Prohibit Optimization (Part-Load Exhaust Temperature & Fuel Splits)
Indirect (Tx Space) Boundary Control
MBC : Direct (Boundary Space) Boundary Control
CPR
TCD
SH
DPxx
CPC
Algorithm

## Slide 17: Load Path to Variable Load Path
T-Exh
GT Load
GT base load
Max. T exh
Simple Cycle Path
Combined Cycle Path
Auto-tune Enabled
Mode 6, Emission Compliant
Min. T- exh
Constant CRT
Constant CRT
Key Enablers for VLP
All Load Auto tune
Feed Forward CAF
Schedule Less Mode Transfers
ALAT
FLP
Next Gen Plant optimization
Increased fuel
flexibility
Increased
operational
flexibility
Optimized plant
startup/ operation

## Slide 18
All-load Autotune
T-Exh
GT Load
GT base load
Max. T exh
Simple Cycle Path
Combined Cycle Path
Auto-tune Enabled
Mode 6,
Emission Compliant
Min. T- exh
T-Exh
GT Load
GT base load
Max. T exh
Auto-tune
Enabled Operating Envelope
Min. T- exh
ALCC
Control
Structure
IGV
FSR
IBH
ARES – GT model
Parameter estimation
Autotune
Control
Structure
DLN Splits
Temperature /
load reference
Emissions /dynamics
reference
Cycle control
Autotune
MBC
All load Autotune
Extend scope of DLN split control below mode 6
  Breaker closure – Base load
  Envelope between SC and CC paths
combustion models
Benefits
Accommodates gas composition variation
  Lower cost than variable fuel heater
Key enabler for Variable Load Path implementation

## Slide 19: Co-ordinated Air Fuel - CAF
Downsides of Current Model-Based CAF
Offline-Generated Path for IGVs (from GTP)
Map is path dependent
Map does not adjust real-time if temps go high/low
Map is based on steady-state data
ARES
Model
mdl
FSR + D
IGV + D
Partial
Derivative
Calc
Expected Benefits
Feedforward term independent of load path
Feedforward term updated real-time based upon actual engine conditions
Combining with Temp control feedback loops will allow for real-time adjustment if/when temps vary from targets/boundaries
Potential to eliminate triggering logic and improve control during normal operation
DTfire
DTexh
Feed-forward term to Temp control loops
Based on idea to move IGV’s so as to counteract temperature impact of FSR
IGV-FF
Traditional MBCAF
Next Gen Model-Based FFCAF Concept

## Slide 20: Feed Forward Calculation
Ex: Tfire, can be done for any ARES output
New ARES model perturbations calculate:
How much Tfire changes with respect to fuel flow and IGV at current conditions
How much IGV movement per unit change in fuel flow will keep Tfire constant
Feed Forward Term
ARES derivatives used to calculate feed forward:
C
G
+
-
FF
+
Targets/ Boundary
Sensor outputs
OR
Model outputs
FF output
+
Controller output

## Slide 21: Mode Transfer Strategy
    When To Transfer?
    Option 1: Fixed CRT
      Transfer? = f (CRT) Current method
    How To Transfer?
    Option 1: Autotune  Split schedule  Autotune Current method
    Option 3: Autotune  Steady State Sol.  Autotune ALAT method

## Slide 22: Mode Transfer in All Load Autotune
Mode Y
Comb. transfer function
MODE X
Fuel system Model
Manifold differential
pressure transducer
PI REG
Priority Selection logic
Comb. transfer function
MODE Y
PI REG
Priority Selection logic
SLEW LOGIC
Mode X
Splits
GT model
Corr. Splits
Corr. Splits
Splits ( in control)
Splits (Not in Control)
Mode select logic
Mode select logic
Int_IN
Splits
Splits
Splits (Not in Control)
Fd.Bck.
Ref
Int_IN
Fd.Bck.
Ref