GE Power

________________________________________________________________________________

## Customer: Exelon Wolf Hollow - Turbine No.  270T932

Subject:   Steam Turbine Customer Software Demonstration Test Plan in Schenectady, NY

Date:

Wolf Hollow – FW19,  2016

This test serves to demonstrate correct functionality of the software in the Mark VIe and HMI operator interfaces.

For the demonstration, the turbine-generator is simulated using an ‘Easy5’ simulation with Artemis. The simulation provides speed, load, pressures, temperatures and valve positions for the testing. A model of the steam turbine has been created to enable exercise of the Mark VIe Turbine Control Software and the HMI screens. Ensure that Artemis is running in real time prior to beginning this test procedure.

With the demonstration, GE verifies and certifies the correct functioning of Mark VIe as follows:

#### Step 1

Introduction and Plan of the Day

Step 2

# Screen Review: The HMI displays are reviewed for familiarity and functional description.  Each screen (if applicable) should be reviewed to ensure that all buttons and hyperlinks are functional.

tp_st_CVIV_Thrust_Lim

tp_st_ADM_Press_Lim_Rate

tp_st_Inlet_Press_Lim_Fixed

tp_st_Inlet_Press_Lim

tp_st_VLV_Pos_Lim

tp_st_IPC_Load_Perm

tp_st_LP_Admission.cim

tp_st_Load_Cmd_Perm

tp_st_Min_Load_perm.cim

tp_st_Permissive.cim

tp_st_Trip_Checks.cim

tp_st_Holds.cim

ST_Auxiliary_Sys.cim

ST_Bearing_Temp.cim

ST_Control.cim

ST_Drains.cim

ST_Hydraulic_fluid.cim

ST_Lube_Seal_Lift_Oil.cim

ST_Monitoring.cim

ST_Overview.cim

ST_Rotor_Stress.cim

ST_Steam_Seal.cim

ST_Test_Mx.cim

ST_Timer_Counter.cim

ST_Turbine_Supervisory.cim

ST_Turbine_Temp.cim

Gen_CapabilityCurves.cim

Gen_EX2100e.cim

Gen_Overview.cim

Gen_Synch.cim

Gen_Temperatures.cim

Step 3

  - Startups and Shutdowns:  Conduct a startup and shutdown. Initial conditions are set to satisfy initial roll conditions.

    - Review Start Permissives HMI Screen – Toggle conditions to show permissives changing

    - Trip on low lube oil pressure.  View trip check screen

    - Remove trip condition and reset. Verify that admission stop valve and main stop valves open. All other valves remain closed

    - Simulate turbine conditions, which will require overriding pre-roll holds (and other holds later). Explain Hold List and its contents. Override all non-simulated holds, if any

    - Acceleration to IPC (use load to IPC command)

    - Select Load to IPC and observe pressure control function, adjust IPC Setpoint to see the control valves respond.

    - Put LP admission into service

    - Slide flow up to increase MW Output

    - Valve Position Limiter setpoint selection, Valve Position Limit limiting occurrence while loading, runs into VPL limit

    - Perform an automatic shutdown by selecting ‘Shutdown’ from the unit control screen.

      - Verify that the unit is automatically taken out of IPC, the load reference command is set to zero and that the control valves begin to close in a controlled manner. Load reference is ramped down over the course of 5 minutes, upon reaching 0.0% the turbine will be tripped and the turbine coasts down toward turning gear.

    - Acceleration with automatic rate selection (show how this changes) and manual speed target selection, wobbulator at 3000 rpm, steady at 3600 rpm speed targets

- Select 3000 rpm from master control. Ensure that the ST speed automatically wobbulates when the speed reaches 3000rpm.

    - Demonstrate manual and automatic speed matching

    - Demonstrate a manual synch of the generator breaker and loading to min load and HP flow mode transfer

    - Demonstrate Load Command Selection, Raise/Lower Load, Operator Loading Rate Selection

    - Demonstrate Transfer to IPC

Step 4

- Aux Controls:

- Steam Seal Pressure Control:

- Start in manual with output set to approximately +50% (SSFV open halfway with SSDV closed)

- Demonstrate 100% output command equates to SSFV full open and -100% output command equates to SSDV full open. 0% equates to both valves full closed

- Place output command back to approximately +50% - select steam seal auto pressure control

- Increase pressure setpoint to approximately 7 psi. Ensure SSFV opens to admit steam

- Lube Oil Temp

- Enter manual mode and ensure bumpless transfer (the output should not change when entering manual mode). Show that as the output is changed, the lube oil temperature control valve modulates in the appropriate direction and the lube oil temperature is adjusted

- Motor Control

- Show that at least 1 of the redundant motors must be running at all times during ST operation. In other words, the operator may not stop one without starting the other

- Drain Valves

- Operate each drain valve via the HMI

- Online Testing

- Valve Tests (showing trender)

- Online ETD Test

- Offline Testing

- From the test and maintenance screen find the offline test section and perform each combination of Offline ETD Tests. 2 out of 3 ETD Tests.

        - Verify that the unit trips and after completion of the test reset the unit and perform the subsequent test.

Conclusion

Review any open items detail any action

Signature Sheet:

Customer:		Exelon

Station:		Wolf Hollow

Turbine No.:	270T932

WITNESSES:  Demonstration results are acceptable to the undersigned.

GE Power:

Exelon:   	____

Date:    	     ____________________________________________________