GE Baseline Security Center

Cybersecurity System Test Procedure

Core Security Module (CSM)

| PRODUCT | BASELINE SECURITY CENTER (BSC) | Revision | #### 1.1 |
| --- | --- | --- | --- |
| SITE | Customer Name – Site Name | DATE | MM/DD/YYYY |
|  |  | PAGES | 25 |

Table of Contents

1.	Introduction	6

2.	Cybersecurity Test Plan	7

2.1	System Readiness & Network Connectivity Verification	7

2.1.1	Ensure System Readiness	7

2.1.2	Verify Control Server Connectivity to the Controls Network Using Echo Request / Ping	7

2.1.3	SMB Connectivity	8

2.1.4	RDP Access	8

2.2	Account Management	9

2.2.1	Default Windows Accounts	9

2.3	System Backup & Recovery	10

2.3.1	Backup Configuration	10

2.3.2	System Backup Task Execution	10

2.3.3	Backup Repository Capacity	11

2.4	Log Aggregation	12

2.4.1	Windows Event Logs	12

2.4.2	Network Device Logging	12

2.5	Network Device Management	13

2.5.1	Secure Access to Network Devices	13

2.6	Application Control (McAfee ePO Orchestrator)	16

2.6.1	Secure Access to McAfee ePO Orchestrator Management Server	16

2.6.2	System Configuration – Asset Organization	16

2.6.3	Blocking Execution of Unapproved Programs & Files	16

2.6.4	Continued Application Control Enforcement Even After Loss of Central Management Server	17

2.6.5	System Configuration – Application Lockdown Status	17

2.6.6	System Configuration – Trusted Updater	17

2.7	SIEM	18

2.7.1	SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards	18

2.7.2	SIEM Device Configuration – Verify Asset Listing	18

2.7.3	SIEM Device Configuration – Verify Data Sources	19

2.7.4	SIEM Device Configuration – Verify Event Logging	19

2.7.5	SIEM Report Generation	19

2.8	Centralized Patch Management & Deployment	20

2.8.1	System Configuration – Asset Organization	20

2.8.2	Patch Status – Control Server & Physical Systems	20

2.8.3	Patch Management Process – Customer Documentation Hand-Off	21

2.9	General System Functionality	22

2.9.1	Time Synchronization	22

2.9.2	Customer Documentation Hand-Off	23

3.	Approvals / Sign-Off	24

3.1	Issue Report Work Sheet	24

Revision History

| Revision | Date | Editor | Revision Summary |
| --- | --- | --- | --- |
| 1 | 05/14/2019 | Jonathan Couch | Initial document release |
| 1.1 | 08/02/2021 | Michael Berube | Updates to test case content |

# Introduction

The purpose of this Cybersecurity System Test (CST) is to verify the proper operation of all equipment for the Site Name-Customer Name project as a system prior to shipment.  The CST procedure verifies:

- Proper system integration of the GE Baseline Security Center (BSC) security appliance

- Expected performance of the GE BSC when integrated with the GE Control Server, GE traditional thick-client HMI equipment, available network equipment and other available GE provided equipment

Procedure Deliverables:

- Signed, completed CST plan

- Supporting documentation highlighting any outstanding / open items at the conclusion of the CST

- Network port scan results of accessible network segments

- GE BSC system configuration documentation (standard ports, services, service accounts and system credential information)

# Cybersecurity Test Plan

The following tests constitute the cybersecurity test plan associated with the implementation of GE’s Baseline Security Center in Control Server system architecture environments.

## System Readiness & Network Connectivity Verification

The following test items are designed to verify general system readiness, availability, and connectivity.

### Ensure System Readiness

| Description: | Verify all physical hosts, virtual machines, network devices, and any available infrastructure equipment (ATS switch, etc.) are available for the test, are connected and are powered on. (Refer to site’s 4108 network topology diagram) |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | Perform review of 4108 drawing |  |  |  |

### Verify Control Server Connectivity to the Controls Network Using Echo Request / Ping

| Description: | Verify that the GE Control Server (hypervisor and all VMs) components are properly connected to the controls network by pinging a sample of the following, as applicable: Item Description; See Asset Checklist for reference. Control Server physical hosts. Control Server VMs. Additional physical HMIs/Historians. Available network devices. |
| --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - |  |  |  |

### SMB Connectivity

| Description: | Verify that the network file access to the default administrative share (\\<SYSTEM_NAME>\C$) can be established over the following connections: - MC3 (Host for BSC Apps) -> Control Server VMs and any additional physical systems running a Windows OS environment. - Control Server VMs / physical systems -> MC3 |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - |  |  |  |

### RDP Access

| Description: | Verify and document hosts that allow RDP access. Disable RDP access where applicable if requested by the customer. List of Hosts: |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference – |  |  |  |

## Account Management

The following test items are designed to verify functionality and configuration of the account management controls in place on the system.

### Default Windows Accounts

| Description: | Verify that the following default Windows user accounts have been deleted or disabled from: - each of the listed domains - a selected local HMI User Account Name; Local HMI; HMI Domain. Administrator. DefaultAccount. Guest. Local HMI Tested: _________________________________ |
| --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

## System Backup & Recovery

The following test items are designed to verify functionality and configuration of the centrally managed backup and restore capabilities provided by the GE BSC 2.0 security system.

### Backup Configuration

| Description: | Verify the following: - Automated backups are configured for each Windows and Linux OS environment to be managed by the GE BSC 2.0 system. - Backup type / contents and backup schedule with the customer representative. - Ensure backup retention period meets customer requirements if customer requirement deviates from standard BSC retention periods. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - |  |  |  |

### System Backup Task Execution

| Description: | Verify a system backup exists for each type of system asset supplied by GE: Asset Type; See Asset Checklist for reference. Control Server VMs. Additional physical HMIs/Historians. BSC VMs. |
| --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - |  |  |  |

### Backup Repository Capacity

| Description: | Verify that the backup repository is provided with sufficient capacity to store, at minimum: - Two (2) generations of backups of all the managed assets, or - The number of backups / retention period specified by any existing customer requirements designed to supersede the BSC default backup retention capacity |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

## Log Aggregation

The following test items are designed to verify functionality and configuration of the log aggregation capabilities provided by the GE BSC security appliance.

### Windows Event Logs

| Description: | Verify the McAfee Log Manager is properly configured to collect Windows Event Logs from each managed asset. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### Network Device Logging

| Description: | Verify that installed network devices capable of logging via Syslog are configured to forward log events to the McAfee SIEM. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Asset Checklist – Network Devices Tab - |  |  |  |

## Network Device Management

The following test items are designed to verify functionality and configuration of the Network Device Management capabilities provided by the GE BSC security appliance.

### Secure Access to Network Devices

| Description: | Using the PuTTY utility to connect to selected switches, perform the following verification: - Verify that connections to network devices to obtain network baseline / configuration data is established via SSH. - Demonstrate the SSH whitelist in the switch configuration - Demonstrate that telnet connections are blocked Network Device IP(s) Tested: ___________________________________ |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

    - RADIUS Functionality.

| Step | Description | Verified | Comments and Observations |
| --- | --- | --- | --- |
| 1 | Review RADIUS in Active Directory on DC1 and DC2 to verify all switches are entered. |  |  |
|  | Date: _________ | Initials________ |  |
| 2 | Verify switches can be accessed with the Active Directory account ‘GESwitch’. |  |  |
|  | Date: _________ | Initials________ |  |
| 3 | Disable RADIUS service on DC1 and DC2 and attempt to log into a switch. When failure occurs, verify switch can be accessed with the local admin account. |  |  |
|  | Date: _________ | Initials________ |  |

    - Cat Tools

| Step | Description | Verified | Comments and Observations |
| --- | --- | --- | --- |
| 1 | Verify all network switches are listed in CatTools. |  |  |
|  | Date: _________ | Initials: _____ |  |
| 2 | Verify all switches can be backed up in CatTools |  |  |
|  | Date: _________ | Initials: _____ |  |
| 3 | Use the reports function to verify any switch changes can be documented. |  |  |
|  | Date: _________ | Initials: _____ |  |
| 5.2.4 | Verify CatTools uses the GESwitch account for accessing the Cisco switches. |  |  |
|  | Date: _________ | Initials: _____ |  |
| 5.2.5 | Verify passwords in CatTools are not stored in plain text |  |  |
|  | Date: _________ | Initials: _____ |  |

    - Switch Logging to SIEM

| Step | Description | Verified | Comments and Observations |
| --- | --- | --- | --- |
| 1 | Verify successful and unsuccessful login attempts are captured in the SIEM. |  |  |
|  | Date: _________ | Initials:_____ |  |
| 2 | Verify switches store logs locally. |  |  |
|  | Date: _________ | Initials:_____ |  |
| 3 | Verify switch time is set for proper NTP source |  |  |
|  | Date: _________ | Initials:_____ |  |

## Application Control (McAfee ePO Orchestrator)

The following test items are designed to verify functionality and configuration of the centrally managed application control capabilities provided by the GE SecurityST security appliance.

### Secure Access to McAfee ePO Orchestrator Management Server

| Description: | Verify that access (via direct URL entry or desktop shortcut) to the McAfee ePO Orchestrator Management Server URL is via HTTPS not HTTP. McAfee ePO can be accessed via direct URL entry at https://mc3:8448/core/orionSplashScreen.do |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### System Configuration – Asset Organization

| Description: | Verify that all managed assets/systems are listed in the McAfee ePO Orchestrator Management Server console and are appropriately grouped / organized. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### Blocking Execution of Unapproved Programs & Files

| Description: | Verify that the McAfee ePO Endpoint client will not open or execute a file that is not on the approved list. Attempting to execute a new unapproved application will have the following results: - Application will fail to run and will generate an error message - An entry will be added to the “Execution Denied” report within EPO Orchestrator |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### Continued Application Control Enforcement Even After Loss of Central Management Server

| Description: | Verify that the deployed application control policy continues to be enforced on managed assets even after the McAfee ePO Orchestrator Management Server is unavailable. To simulate – On the MC3 server, stop the “McAfee ePolicy Orchestrator 5.10.0 Application Server & McAfee\ePolicy Orchestrator” service from the Service management console. And then verify the functionality. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### System Configuration – Application Lockdown Status

| Description: | Verify that all managed assets/systems are configured with Solid Core in Observe Mode prior to shipment to site for commissioning. This will avoid complications during site installation. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Asset Checklist |  |  |  |

### System Configuration – Trusted Updater

| Description: | Verify that the WorkstationST.exe executable is defined as a Trusted Updater and that this setting has been propagated to all the HMI’s running ControlST. System Tree – Assigned Policies – Product-Solidcore 8.3.2:App Control, Application Control Rules (Windows) – GE Default Select ControlST under My Rules Left Pane This configuration change ensures that the Static Starter and Exciter screens fully operate. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

## SIEM

The following test items are designed to verify functionality and configuration of the Security Incident and Event Monitoring (SIEM) capabilities provided by the GE BSC security appliance.

### SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards

| Description: | - Demonstrate the following widgets are displayed on the GE Default dashboard & are populated with event data: - Windows Device Events - Network Device Events - VMWare Device Events - Event Summary - Event count by Host - Events - Open the NERC-CIP 002 Dashboard and confirm the widgets are populating with event data |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### SIEM Device Configuration – Verify Asset Listing

| Description: | Verify that all applicable assets are listed in the McAfee SIEM appliance, and are populated within their respective Asset Groups defined below: - VMWare - Windows - Network Devices |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### SIEM Device Configuration – Verify Data Sources

| Description: | Verify that all applicable data sources are listed in the McAfee SIEM appliance, and the correct properties are assigned to each one. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### SIEM Device Configuration – Verify Event Logging

| Description: | Verify that an event is displayed in the Windows Login Events widget of the GE Default Dashboard after a successful or invalid login attempt. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### SIEM Report Generation

| Description: | Verify that a selected report can be generated and contains relevant event data. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

## Centralized Patch Management & Deployment

The following test items are designed to verify functionality and configuration of the centrally managed patch deployment capabilities provided by the GE BSC security appliance.

Note:  This section is only applicable in situations where the centralized patch management and deployment solution is included with the BSC security appliance.

### System Configuration – Asset Organization

| Description: | Verify that all managed assets/systems are listed in the Ivanti Patch for Windows management console and are appropriately grouped / organized. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Asset Checklist - |  |  |  |

### Patch Status – Control Server & Physical Systems

| Description: | Verify the latest validated patches for installation on Windows OS environments have been applied to the Control Server Windows-based virtual machines and any Windows-based physical HMIs/Historians. Windows assets - Open Ivanti Patch for Windows management console - Run a scan of desired Asset Group Date of Patch Disc Applied: ____________________________ (Must login as Domain Admin) |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Asset Checklist - |  |  |  |

### Patch Management Process – Customer Documentation Hand-Off

| Description: | Provide hand-off materials to the customer representative documenting GE BSC standard procedure for obtaining and applying validated patches as part of the Power Patch Validation Program. - DisPatch Web Portal User’s Guide - BSC Windows Patching Guide |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

## General System Functionality

The following test items are designed to verify general system functionality and configuration of the GE BSC security appliance not captured elsewhere.

### Time Synchronization

| Description: | Verify that the DC1 and DC2 servers are configured to synchronize time with the available NTP time server(s) on the GE controls network, as per the GE 4108 network topology drawing. (192.168.201.250) - Login to DC1 and DC2 server - At a Command prompt, type – w32tm /query /configuration - At a Command prompt, type – w32tm /query /status Verify the hypervisor is set to receive its time synchronization from an available Domain Controller server(s) on the GE controls network. (DC1, DC2) - Using the Chrome browser, access the vCenter Server via the VMware vSphere Client located at https://192.168.201.114/ui - Login to the vCenter Server with proper credentials - Select “Hosts and Clusters” view from left pane - Select the Hypervisor from the table below VM Name; IP Address; Confirm Time Configuration Settings. HS1; 192.168.201.118. HS2; 192.168.201.119. HW1; 192.168.201.110. MC2; 192.168.201.111. BSC-HV1A; 192.168.201.114. - Select the “Configure” Tab in the Main Panel - Open the “System” Option - Select the “Time Configuration” sub-option - Confirm the following settings: - NTP Client – Enabled - NTP Service Status - Running - NTP Servers - set to the proper Domain Controller Server IP addresses per the GE 4108 network topology drawing. Verify that all other non-Windows VMs are configured to receive their time synchronization from the physical host on which they reside. Steps to verify: - Right-click on VM of interest from list below - Select – Edit Settings - Select the “VM Options” tab - Expand the “VMWare Tools” option - Time setting – verify “Synchronize guest time with host” is checked Non-Windows VM Name; Confirm Time Synchronization Settings. Acronis_VA_HS1*. Acronis_VA_HS2*. Acronis_VA_MC2*. Acronis _VA_BSC-HV1A. ENMELM. EDGE1SVR. HC1*. HW1*. * Not all VMs may be present based on the type of control solution being provided as part of the project. For example, BU1, BU2 and BU3 will only be present in environments where a GE Control Server is being provided, and the customer has opted to include the Acronis backup and recovery solution. |
| --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

### Customer Documentation Hand-Off

| Description: | Provide hand-off materials to the customer representative documenting GE BSC standard ports, services, service accounts and system credential information, as applicable. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Michael Berube | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | Upload all relevant docs to GE Box folder for this project. |  |  |  |

# Approvals / Sign-Off

______	GE BSC cybersecurity factory system test completed and approved with no outstanding / open items

______	GE BSC cybersecurity factory system test completed and approved with outstanding / open items still to complete (refer to documented punch list / action items list below

## Issue Report Work Sheet

| Issue # | Issue Description | Report Date | Assigned To | Expected Closure Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |

Signed for: 	Signed for:

GE Cyber Security Representative	Customer Representative

Signature:_____Michael Berube_________________	Signature:	__________________________________

Name (Printed):___Michael Berube______________	Name (Printed):	_____________________________

Date:_______________________________________	Date:	______________________________________