GE Baseline Security Center

Cybersecurity System Test Procedure

Core Security Module (CSM)

| PRODUCT | BASELINE SECURITY CENTER (BSC) | Revision | #### 2.0 |
| --- | --- | --- | --- |
| SITE | Sharqiyah Hawiyah Cogen | DATE | 09/05/2024 |
|  |  | PAGES | 27 |

Table of Contents

1.	Introduction	6

2.	Cybersecurity Test Plan	7

2.1	System Readiness & Network Connectivity Verification	7

2.1.1	Ensure System Readiness	7

2.1.2	Verify Control Server Connectivity to the Controls Network Using Echo Request / Ping	7

2.1.3	SMB Connectivity	8

2.1.4	RDP Access	8

2.2	Account Management	9

2.2.1	Default Windows Accounts	9

2.3	System Backup & Recovery	10

2.3.1	Backup Configuration	10

2.3.2	System Backup Task Execution	10

2.3.3	Backup Repository Capacity	11

2.3.4	Restore a File from Backup	11

2.3.5	Restore a Folder from Backup	11

2.3.6	Restore a Virtual Machine from Backup	12

2.4	Log Aggregation	13

2.4.1	Windows Event Logs	13

2.4.2	Network Device Logging	13

2.5	Network Device Management	14

2.5.1	Secure Access to Network Devices	14

2.6	Application Control (Trellix ePO Orchestrator)	17

2.6.1	Secure Access to Trellix ePO Orchestrator Management Server	17

2.6.2	System Configuration – Asset Organization	17

2.6.3	Blocking Execution of Unapproved Programs & Files	17

2.6.4	Continued Application Control Enforcement Even After Loss of Central Management Server	18

2.6.5	System Configuration – Application Lockdown Status	18

2.6.6	System Configuration – Trusted Updater	18

2.6.7	System Configuration – Trellix AV Definitions Staged in Main Repository	19

2.6.8	System Configuration – Trellix AV Definitions Deployed to Managed Assets	19

2.6.9	System Configuration – Detection of EICAR AV Test File	19

2.7	SIEM	20

2.7.1	SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards	20

2.7.2	SIEM Device Configuration – Verify Asset Listing	20

2.7.3	SIEM Device Configuration – Verify Data Sources	21

2.7.4	SIEM Device Configuration – Verify Event Logging	21

2.7.5	SIEM Report Generation	21

2.8	Centralized Patch Management & Deployment	22

2.8.1	System Configuration – Asset Organization	22

2.8.2	Patch Status – Control Server & Physical Systems	22

2.8.3	Patch Management Process – Customer Documentation Hand-Off	23

2.9	General System Functionality	24

2.9.1	Time Synchronization	24

3.	Approvals / Sign-Off	25

3.1	Issue Report Work Sheet	25

Revision History

| Revision | Date | Editor | Revision Summary |
| --- | --- | --- | --- |
| 1 | 05/14/2019 | Jonathan Couch | Initial document release |
| 1.1 | 08/02/2021 | Michael Berube | Updates to test case content |
| 2.0 | 07/12/2023 | Michael Berube | Added 3 test cases for Acronis Restoration |
| 2.1 | 09/14/2023 | Michael Berube | Removed HW1 VM from Non-Windows VM Name table in Test Case 2.9.1 |
| 2.2 | 02/07/2024 | Michael Berube | Added test cases for: - CatTools Device.Backup.Running Config Activity - CatTools System.File.Delete Activity - ePO AMCore Definitions staged in Repository - ePO AMCore Definitions deployed to assets - ePO AV Test using eicar tool |
| 2.3 | 09/05/2024 | Nathan Ridgeway | Edited for Sharqiyah Hawiyah Cogen |

# Introduction

The purpose of this Cybersecurity System Test (CST) is to verify the proper operation of all equipment for the Tenaska - Frontier project as a system prior to shipment.  The CST procedure verifies:

- Proper system integration of the GE Baseline Security Center (BSC) security appliance

- Expected performance of the GE BSC when integrated with the GE Control Server, GE traditional thick-client HMI equipment, available network equipment and other available GE provided equipment

Procedure Deliverables:

- Signed, completed CST plan

- Supporting documentation highlighting any outstanding / open items at the conclusion of the CST

- Network port scan Result of accessible network segments

- GE BSC system configuration documentation (standard ports, services, service accounts and system credential information)

# Cybersecurity Test Plan

The following tests constitute the cybersecurity test plan associated with the implementation of GE’s Baseline Security Center in Control Server system architecture environments.

## System Readiness & Network Connectivity Verification

The following test items are designed to verify general system readiness, availability, and connectivity.

### Ensure System Readiness

| Description: | Verify all physical hosts, virtual machines, network devices, and any available infrastructure equipment (ATS switch, etc.) are available for the test, are connected and are powered on. (Refer to site’s 4108 network topology diagram) |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Perform review of 4108 drawing- Refer to document “Result – 2.1.1-2_DNS Test.txt” |  |  |  |

### Verify Control Server Connectivity to the Controls Network Using Echo Request / Ping

| Description: | Verify that the GE Control Server (hypervisor and all VMs) components are properly connected to the controls network by pinging a sample of the following, as applicable: Item Description; See Asset Checklist for reference. Control Server physical hosts. Control Server VMs. Additional physical HMIs/Historians. Available network devices. |
| --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference – Refer to document “Result – 2.1.1-2_DNS Test.txt” |  |  |  |

### SMB Connectivity

| Description: | Verify that the network file access to the default administrative share (\\<SYSTEM_NAME>\C$) can be established over the following connections: - WIN1SVR (Host for BSC Apps) -> Control Server VMs and any additional physical systems running a Windows OS environment. - Control Server VMs / physical systems -> WIN1SVR |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - Refer to document “Result – 2.1.3_SMB.txt” |  |  |  |

### RDP Access

| Description: | Verify and document hosts that allow RDP access. Disable RDP access where applicable if requested by the customer. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference – Refer to document “Result – 2.1.4_RDP.txt” |  |  |  |

## Account Management

The following test items are designed to verify functionality and configuration of the account management controls in place on the system.

### Default Windows Accounts

| Description: | Verify that the following default Windows user accounts have been deleted or disabled from: - each of the listed domains - a selected local HMI User Account Name; Local HMI; HMI Domain. Administrator. DefaultAccount. Guest. Local HMI Tested: All |
| --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to document “Result – 2.2.1_Default Accounts.txt” |  |  |  |

## System Backup & Recovery

The following test items are designed to verify functionality and configuration of the centrally managed backup and restore capabilities provided by the GE BSC 2.0 security system.

### Backup Configuration

| Description: | Verify the following: - Automated backups are configured for each Windows and Linux OS environment to be managed by the GE BSC 2.0 system. - Backup type / contents and backup schedule with the customer representative. - Ensure backup retention period meets customer requirements if customer requirement deviates from standard BSC retention periods. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference – Refer to document “Result - 2.3.1_Backup Plans.rtf” |  |  |  |

### System Backup Task Execution

| Description: | Verify a system backup exists for each type of system asset supplied by GE: Asset Type; See Asset Checklist for reference. Control Server VMs. Additional physical HMIs/Historians. BSC VMs. |
| --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - Refer to document “Result – 2.3.2_NAS Backup Contents.txt” |  |  |  |

### Backup Repository Capacity

| Description: | Verify that the backup repository is provided with sufficient capacity to store, at minimum: - The GE standard retention scheme – 6 x Monthly FULL, 4 x Weekly DIFF, 7 x Daily INCREMENTAL backups of all the managed assets, or - The number of backups / retention period specified by any existing customer requirements designed to supersede the BSC default backup retention capacity |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result - 2.3.3_Backup Storage.PNG” |  |  |  |

### Restore a File from Backup

| Description: | Verify a file from an existing Acronis backup can be restored from the backup repository. - Recover the putty.exe file from the BSC Mgmt VM (usually MC3) - Restore the file to the Downloads folder |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.3.4_File Recovery.PNG” |  |  |  |

### Restore a Folder from Backup

| Description: | Verify a folder of files from an existing Acronis backup can be restored from the backup repository. - Recover the C:\McAfee\Definitions folder from the BSC Mgmt VM (usually MC3) - Restore the file to the C:\Temp folder |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.3.5_Folder Recovery.PNG” |  |  |  |

### Restore a Virtual Machine from Backup

| Description: | Verify a Virtual Machine image from an existing Acronis backup can be restored from the backup repository. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.3.6_VM Recovery.rtf” |  |  |  |

## Log Aggregation

The following test items are designed to verify functionality and configuration of the log aggregation capabilities provided by the GE BSC security appliance.

### Windows Event Logs

| Description: | Verify the Trellix Log Manager is properly configured to collect Windows Event Logs from each managed asset. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 9/5/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “2.4.1_Windows Logs.rtf” |  |  |  |

### Network Device Logging

| Description: | Verify that installed network devices capable of logging via Syslog are configured to forward log events to the Trellix SIEM. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 9/5/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.4.2_Switch Logs.rtf” |  |  |  |

## Network Device Management

The following test items are designed to verify functionality and configuration of the Network Device Management capabilities provided by the GE BSC security appliance.

### Secure Access to Network Devices

| Description: | Using the PuTTY utility to connect to selected switches, perform the following verification: - Verify that connections to network devices to obtain network baseline / configuration data is established via SSH. - Demonstrate the SSH whitelist in the switch configuration - Demonstrate that telnet connections are blocked Network Device IP(s) Tested: All |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.5.1_Switch Access.txt” |  |  |  |

    - RADIUS Functionality.

| Step | Description | Verified | Comments and Observations |
| --- | --- | --- | --- |
| 1 | Review RADIUS in Active Directory on DC1 and DC2 to verify all switches are entered. |  | Refer to Document “Result – 2.5.2_RADIUS.docx” |
|  | Date: 09/05/2024 | Initials NAR |  |
| 2 | Verify switches can be accessed with the Active Directory account ‘GESwitch’. |  | Shown via CatTools in document “Result – 2.5.1_Switch Access.txt” |
|  | Date: 09/05/2024 | Initials NAR |  |
| 3 | Disable RADIUS service on DC1 and DC2 and attempt to log into a switch. When failure occurs, verify switch can be accessed with the local admin account. |  | Refer to document “Result - 2.5.2_Admin No Radius.PNG” |
|  | Date: 09/05/2024 | Initials NAR |  |

    - Cat Tools

| Step | Description | Verified | Comments and Observations |
| --- | --- | --- | --- |
| 1 | Verify all network switches are listed in CatTools. |  | Refer to Document “Result – 2.5.3A_CatTools Devices.PNG” |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 2 | Verify all switches can be backed up in CatTools |  | Refer to Document “Result – 2.5.1_Switch Access.txt” |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 3 | Use the reports function to verify any switch changes can be documented. |  | Refer to Document “Result - 2.5.3B_Reports.txt” |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 4 | Verify CatTools uses the GESwitch account for accessing the Cisco switches. |  | TEST PASS (screenshot not possible) |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 5 | Verify passwords in CatTools are not stored in plain text |  | Refer to Document “Result – 2.5.3C_Password Plain Text.PNG” |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 6 | Verify the Device.Backup.Running Config activity is present and configured to perform backups at least once per week. |  | Refer to Document “Result - 2.5.3D_Backup Activity.PNG” |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 7 | Verify the System.File.Delete activity is present and configured as follows: - Time tab: Reoccurring – “Every 1st day of the Month” - Options tab: - "Number of device specific dated files to retain" – set to 6 - "Delete files older than how many days" – set to 30 |  | Refer to Document “Result - 2.5.3E_Retention.rtf” |

    - Switch Logging to SIEM

| Step | Description | Verified | Comments and Observations |
| --- | --- | --- | --- |
| 1 | Verify successful and unsuccessful login attempts are captured in the SIEM. |  | Refer to Document “Result - 2.5.4A_Log-On Log.rtf” |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 2 | Verify switches store logs locally. |  | Refer to Document “Result - 2.5.4B_Local Logs.rtf” |
|  | Date: 09/05/2024 | Initials: NAR |  |
| 3 | Verify switch time is set for proper NTP source |  | Refer to Document “Result - 2.5.4C_TimeSync.rtf” |
|  | Date: 09/05/2024 | Initials: NAR |  |

## Application Control (Trellix ePO Orchestrator)

The following test items are designed to verify functionality and configuration of the centrally managed application control capabilities provided by the GE SecurityST security appliance.

### Secure Access to Trellix ePO Orchestrator Management Server

| Description: | Verify that access (via direct URL entry or desktop shortcut) to the Trellix ePO Orchestrator Management Server URL is via HTTPS not HTTP. Trellix ePO can be accessed via direct URL entry at https://mc3:8448/core/orionSplashScreen.do |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.6.1_ePOHTTPS.PNG” |  |  |  |

### System Configuration – Asset Organization

| Description: | Verify that all managed assets/systems are listed in the Trellix ePO Orchestrator Management Server console and are appropriately grouped / organized. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - Refer to Document “Result – 2.6.2_ePO Assets.PNG” |  |  |  |

### Blocking Execution of Unapproved Programs & Files

| Description: | Verify that the Trellix ePO Endpoint client will not open or execute a file that is not on the approved list. Attempting to execute a new unapproved application will have the following Result: - Application will fail to run and will generate an error message - An entry will be added to the “Execution Denied” report within EPO Orchestrator |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result - 2.6.3_Execution Blocked.PNG” |  |  |  |

### Continued Application Control Enforcement Even After Loss of Central Management Server

| Description: | Verify that the deployed application control policy continues to be enforced on managed assets even after the Trellix ePO Orchestrator Management Server is unavailable. To simulate – On the MC3 server, stop the “Trellix ePolicy Orchestrator 5.10.0 Application Server & Trellix\ePolicy Orchestrator” service from the Service management console. And then verify the functionality. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result - 2.6.4_ePO Disabled.PNG” |  |  |  |

### System Configuration – Application Lockdown Status

| Description: | Verify that all managed assets/systems are configured with Solid Core in Observe or Inventory Mode prior to shipment to site for commissioning. This will avoid complications during site installation. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Asset Checklist - Refer to document “Result – 2.6.5_InventoryMode.txt” |  |  |  |

### System Configuration – Trusted Updater

| Description: | Verify that the WorkstationST.exe executable is defined as a Trusted Updater and that this setting has been propagated to all the HMI’s running ControlST. System Tree – Assigned Policies – Product-Solidcore 8.3.2:App Control, Application Control Rules (Windows) – GE Default Select ControlST under My Rules Left Pane This configuration change ensures that the Static Starter and Exciter screens fully operate. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result - 2.6.6_App Control Rules.PNG” |  |  |  |

### System Configuration – Trellix AV Definitions Staged in Main Repository

| Description: | Verify a recent AMCore Content Package has been checked in to the Trellix ePO Main Repository. - Select ePO Menu icon – Software-Main Repository - Confirm an AMCore Content Package is listed in the Name column and the Branch column indicates “Current” |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.6.7_AMCore.PNG” |  |  |  |

### System Configuration – Trellix AV Definitions Deployed to Managed Assets

| Description: | Verify the recent AMCore Content Package observed in the Main Repository (see previous test case) has been deployed to all managed assets. - Select Dashboards from the ePO Main Menu - Select “Endpoint Security: Content Status” from the drop-down list - Click on the version number in the AMCore Content version column to display all the assets that have this version installed (This should be all managed assets) - Confirm there are no assets missing an AMCore Content Package |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - Refer to Document “Result – 2.6.8_Assets AMCore.PNG” |  |  |  |

### System Configuration – Detection of EICAR AV Test File

| Description: | Verify the Trellix AV software can detect and block execution of the EICAR test file - Open Notepad on the BSC VM. - Copy the following text string into the Notepad file: - X5O!P%@AP[4\PZX54(P^)7CC)7}$EICAR-STANDARD-ANTIVIRUS-TEST-FILE!$H+H* - Attempt to save the file to the Downloads folder or any local folder as eicar.txt - The Trellix software will perform an On-Access scan and display a pop-up message that a threat was detected and the file was deleted. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | See Asset Checklist for reference - Refer to document “Result – 2.6.9_EICAR.txt” |  |  |  |

## SIEM

The following test items are designed to verify functionality and configuration of the Security Incident and Event Monitoring (SIEM) capabilities provided by the GE BSC security appliance.

### SIEM Dashboards – GE Default Dashboard & NERC-CIP Dashboards

| Description: | - Demonstrate the following widgets are displayed on the GE Default dashboard & are populated with event data: - Windows Device Events - Network Device Events - VMWare Device Events - Event Summary - Event count by Host - Events - Failed Login by User - Open the NERC-CIP 002 Dashboard and confirm the widgets are populating with event data |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.7.1_ESM Dashboard.PNG” |  |  |  |

### SIEM Device Configuration – Verify Asset Listing

| Description: | Verify that all applicable assets are listed in the Trellix SIEM appliance, and are populated within their respective Asset Groups defined below: - VMWare - Windows - Network Devices |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.7.2_Asset Manager.rtf” |  |  |  |

### SIEM Device Configuration – Verify Data Sources

| Description: | Verify that all applicable data sources are listed in the Trellix SIEM appliance, and the correct properties are assigned to each one. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.7.3_Data Sources.rtf” |  |  |  |

### SIEM Device Configuration – Verify Event Logging

| Description: | Verify that an event is displayed in the Windows Login Events widget of the GE Default Dashboard after a successful or invalid login attempt. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.7.4_Login Attempt.PNG” |  |  |  |

### SIEM Report Generation

| Description: | Verify that a selected report can be generated and contains relevant event data. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Document “Result – 2.7.5_Reports.PNG” |  |  |  |

## Centralized Patch Management & Deployment

The following test items are designed to verify functionality and configuration of the centrally managed patch deployment capabilities provided by the GE BSC security appliance.

Note:  This section is only applicable in situations where the centralized patch management and deployment solution is included with the BSC security appliance.

### System Configuration – Asset Organization

| Description: | Verify that all managed assets/systems are listed in the Ivanti Patch for Windows management console and are appropriately grouped / organized. |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Asset Checklist – Refer to Document “Result – 2.8.1_Machine Groups.PNG” |  |  |  |

### Patch Status – Control Server & Physical Systems

| Description: | Verify the latest validated patches for installation on Windows OS environments have been applied to the Control Server Windows-based virtual machines and any Windows-based physical HMIs/Historians. Windows assets - Open Ivanti Patch for Windows management console - Run a scan of desired Asset Group Date of Patch Disc Applied: M624 (Must login as Domain Admin) |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to Asset Checklist – Refer to Document “Result – 2.8.2_Patch Status.PNG” |  |  |  |

### Patch Management Process – Customer Documentation Hand-Off

| Description: | Provide hand-off materials to the customer representative documenting GE BSC standard procedure for obtaining and applying validated patches as part of the Power Patch Validation Program. - DisPatch Web Portal User’s Guide - BSC Windows Patching Guide |  |  |  |
| --- | --- | --- | --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: |  |
|  | Customer Representative: |  | Date: |  |
| Comments: |  |  |  |  |

## General System Functionality

The following test items are designed to verify general system functionality and configuration of the GE BSC security appliance not captured elsewhere.

### Time Synchronization

| Description: | Verify that the DC1 and DC2 servers are configured to synchronize time with the available NTP time server(s) on the GE controls network, as per the GE 4108 network topology drawing. (192.168.201.250) - Login to DC1 and DC2 server - At a Command prompt, type – w32tm /query /configuration - At a Command prompt, type – w32tm /query /status Verify the hypervisor is set to receive its time synchronization from an available Domain Controller server(s) on the GE controls network. (DC1, DC2) - Using the Chrome browser, access the vCenter Server via the VMware vSphere Client located at https://192.168.201.114/ui - Login to the vCenter Server with proper credentials - Select “Hosts and Clusters” view from left pane - Select the Hypervisor from the table below VM Name; IP Address; Confirm Time Configuration Settings. HS1; 172.16.199.8. HS2; 172.16.199.9. HW1; 172.16.199.10. MC2; 172.16.199.11. - Select the “Configure” Tab in the Main Panel - Open the “System” Option - Select the “Time Configuration” sub-option - Confirm the following settings: - NTP Client – Enabled - NTP Service Status - Running - NTP Servers - set to the proper Domain Controller Server IP addresses per the GE 4108 network topology drawing. Verify that all other non-Windows VMs are configured to receive their time synchronization from the physical host on which they reside. Steps to verify: - Right-click on VM of interest from list below - Select – Edit Settings - Select the “VM Options” tab - Expand the “VMWare Tools” option - Time setting – verify “Synchronize guest time with host” is checked Non-Windows VM Name; Confirm Time Synchronization Settings. Acronis_VA_HS1*. Acronis_VA_HS2*. Acronis_VA_MC2*. * Not all VMs may be present based on the type of control solution being provided as part of the project. For example, BU1, BU2 and BU3 will only be present in environments where a GE Control Server is being provided, and the customer has opted to include the Acronis backup and recovery solution. |
| --- | --- |
| Sign-Off: | Test Engineer: | Nathan Ridgeway | Date: | 09/05/2024 |
|  | Customer Representative: |  | Date: |  |
| Comments: | Refer to document “Result – 2.9.1_TimeSync.txt” |  |  |  |

# Approvals / Sign-Off

______	GE BSC cybersecurity factory system test completed and approved with no outstanding / open items

______	GE BSC cybersecurity factory system test completed and approved with outstanding / open items still to complete (refer to documented punch list / action items list below

## Issue Report Work Sheet

| Issue # | Issue Description | Report Date | Assigned To | Expected Closure Date | Status |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |

Signed for: 	Signed for:

GE Cyber Security Representative	Customer Representative

Signature:_____Nathan Ridgeway_________________	Signature:	__________________________________

Name (Printed):___Nathan Ridgeway______________	Name (Printed):	_____________________________

Date:___09/05/2024_______________________	Date:	______________________________________